## Battery Calc Sheet
Battery Calculation Worksheet
Project Name
Project Number
|  |  |  | 1 | 2-60 | 61-120 | 121-180 | 181-239 | 240
Plant Battery Voltage | 125 |  | Elapsed Time (minutes) | 1 | 60 | 120 | 180 | 239 | 240
Margin | 10% |  | Duration (minutes) | 1 | 59 | 60 | 60 | 59 | 1
SERVICE | QUANTITY | RUN AMPS | NORMAL AMPS | DUTY CYCLE AMPS
Steam Turbine
Emergency Lube Oil Pump | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency Seal Oil Pump | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generator Protection Relay Panel | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Relay Panels
Lock Out Relay for Generator and Breaker | 2 | 4.63 | 0 | 9.26 | 0 | 0 | 0 | 0 | 0
Relay and Metering Panels | 2 | 7 | 14 | 14 | 14 | 14 | 14 | 14 | 14
|  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Control System
Misc Control Panels | 2 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Control Room Equipment | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DCS Cabinet | 15 | 10 | 150 | 150 | 150 | 150 | 150 | 150 | 150
PLC | 2 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Electrically Operated Breakers
Medium Voltage Breaker (Trip) | 29 | 10 | 0 | 290 | 0 | 0 | 0 | 0 | 0
Medium Voltage Breaker (Close) | 29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 348
Medium Voltage Switchgear (Normal) | 2 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Low Voltage Breaker (Trip) | 29 | 3 | 0 | 87 | 0 | 0 | 0 | 0 | 0
Low Voltage Breaker (Close) | 29 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 290
Low Voltage Switchgear (Normal) | 4 | 3 | 12 | 12 | 12 | 12 | 12 | 12 | 12
Generator Circuit Breaker (Trip) | 1 | 12.6 | 0 | 12.6 | 0 | 0 | 0 | 0 | 0
Generator Circuit Breaker (Close) | 1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3
Generator Circuit Breaker (Charging Motor) | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 4
Transformers
Generator Step-Up Transformer Relay | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Unit Auxiliary Transformer Relay | 2 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6
SUS Transformer Relay | 6 | 3 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Emergency Diesel Generator
EDG Panel (Idle) | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1
EDG Panel (In Operation) | 1 | 5 | 0 | 0 | 5 | 5 | 5 | 5 | 0
Low Voltage Breaker (Close) | 1 | 10 | 0 | 10 | 0 | 0 | 0 | 0 | 0
Switchyard Equipment
High Voltage Circuit Breaker (Trip) | 1 | 14 | 0 | 14 | 0 | 0 | 0 | 0 | 0
High Voltage Circuit Breaker (Close) | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 10
High Voltage Circuit Breaker (Normal) | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0
Switchyard Relay Panel | 1 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Graph includes margin
Misc.
UPS | 1 | 368.7 | 368.7 | 368.7 | 368.7 | 368.7 | 368.7 | 368.7 | 368.7
Fire Panel | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Load (A) |  |  | 612.7 | 1034.56 | 616.7 | 616.7 | 616.7 | 616.7 | 1266
10% Margin |  |  | 61.27 | 103.456 | 61.67 | 61.67 | 61.67 | 61.67 | 126.6
Total w/ Design Margin (A) |  |  | 673.97 | 1138.016 | 678.37 | 678.37 | 678.37 | 678.37 | 1392.6
Battery Charger Calculation
Recharging Time (hours) | 24 |  | Amp-Hour Ratings
Minimum Battery Charger Capacity (A) | 830.5507 |  |  | 17.2427 | 606.4217 | 616.7 | 616.7 | 606.4217 | 21.1
Rated Battery Charger Capacity (A) | 850 |  | Base Battery Capacity (Cb) | [5 empty] | 2484.586
|  |  | Design Margin | [5 empty] | 10%
|  |  | Temperature Correction Factor | [5 empty] | 1
|  |  | Age Factor | [5 empty] | 1.25
|  |  | Expected Battery Size (Ah minimum) | [5 empty] | 3416.3057
1.1 = Recharging Factor for Lead Acid Battery Type
L = plant load at normal conditions (Normal Amps)
C = Ampere hours emergency discharge (Total Ah)
H = number of hours recharge time required per contract
Cb = Battery Base Capacity
DM = Design Margin
T = Temperature Correction Factor
A = Age Factor
Note on B18: Note: Number of Generators
Note on B22: Note: Quantity of 1 is Normal
Note on B23: Note: Quantity of 1 unless fed from UPS which is typical
Note on B24: Note: Number of DCS cabinet locations (typically 6 for a 2x1) (0 if fed from UPS)
Note on B25: Note: Typically fed from UPS
Note on B28: Note: Insert Number of Main Breakers
Note on B30: Note: Insert Number of Lineups
Note on B31: Note: Insert Number of Main Breakers
Note on B33: Note: Insert Number of Lineups
Note on B39: Note: Insert Number of GSUs
Note on B40: Note: Insert Number of UATs
Note on B41: Note: Insert Number of UATs
Note on C54: Note: DC Load KVA value from UPS Calc Sheet.
Note on B55: Note: Haynes had 4.
Note on D59: Adam.Reab: This cell is for battery charger sizing and should include margin

## UPS Calc Sheet
UPS Calculation Worksheet
Project Name
Project Number
Plant UPS Voltage | 120 | Efficiency |  |  | 88%
Margin | 20% | Single Phase
SERVICE | QUANTITY | AMPS | KVA | Demand | Demand KVA
Steam Turbine
Hydrogen Monitor Cabinet | 0 | 5 | 0 | 0.95 | 0
Mark VI Control Panel | 1 | 16 | 1.92 | 0.95 | 1.824
Workstation | 1 | 6 | 0.72 | 0.7 | 0.504
Combustion Turbine
Workstation | 1 | 10 | 1.2 | 0.7 | 0.84
HRSG
LP Drum Remote Level Element | 2 | 0.5 | 0.12 | 0.95 | 0.114
IP Drum Remote Level Element | 2 | 0.5 | 0.12 | 0.95 | 0.114
HP Drum Remote Level Element | 2 | 0.5 | 0.12 | 0.95 | 0.114
Drum Water Level Gauge Control Panel | 1 | 8 | 0.96 | 0.95 | 0.912
Control System
DCS Cabinets | 15 | 10 | 18 | 0.95 | 17.1
Engineering Workstation | 1 | 5 | 0.6 | 0.4 | 0.24
Historian Workstation/Server | 1 | 5 | 0.6 | 0.4 | 0.24
Operator Workstation | 3 | 5 | 1.8 | 0.7 | 1.26
Printer | 2 | 4 | 0.96 | 0.25 | 0.24
Network Cabinet | 1 | 3 | 0.36 | 0.95 | 0.342
PLCs | 5 | 10 | 6 | 0.95 | 5.7
Misc.
Solenoid Valves | 200 | 6.6 | 158.4 | 0.05 | 7.92
CEMS Power | 1 | 18 | 2.16 | 0.95 | 2.052
CEMS Log Printer | 1 | 3.5 | 0.42 | 0.25 | 0.105
CEMS OWS | 1 | 7 | 0.84 | 0.4 | 0.336
Communications/Telephone | 1 | 10 | 1.2 | 0.5 | 0.6
Totals
Total |  |  | 196.5 |  | 40.557
| UPS KVA | DC Load KVA
Total Load | 40.557 | 40.557
Efficiency 88% |  | 46.0875
Plus 20% Margin | 8.1114 | 9.2175
Totals | 48.6684 | 55.305
UPS Chosen | 50 | KVA |  |  |  | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60
Note on B17: Note: Quantity of HRSGs.
Note on B20: Note: Zero out if there are no HRSGs on the project.
Note on B23: Note: (typically 6 for 2x1) (0 if fed from Battery)
Note on B29: Note: (Include Duct Burner PLC, Air Compressor PLC, and CEMs PLC)

## Battery Rollup (hidden)
| Thorold |  |  |  | Panoche |  |  |  | Bartow 4X1 |  |  |  | Hines 3 |  |  |  | Hines 4 |  |  |  | Palomar |  |  |  | GDMEC |  |  |  | Haynes |  |  |  | DPPP
| 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal | 1st Minute | Duration | Last Minute | Normal
SF6 HV Bkr Trip Coil 1 | [8 empty] | 10.5 | 1 | 23 | 1 | 14.4 |  |  |  | 14.4 | [15 empty] | 13.2 | 1 | 0 | 1
SF6 HV Bkr Trip Coil 2 | [8 empty] | 10.5 | 1 | 23 | 1 | 14.4 |  |  |  | 14.4
SF6 HV Bkr Close Coil | [14 empty] | 3.8 |  |  |  | 3.8 | [13 empty] | 0 | 0 | 19.8 | 0
GSU Relay |  |  |  |  | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2
UAT Relay |  |  |  |  | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 10 | 10 | 10 | 10 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2
MV Bkr Trip | 60 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 10.5 | 1 | 0 | 1
MV Bkr Close | 0 | 0 | 72 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 23 | 0
MV SWGR/MCC | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5
LV Bkr Trip | 12 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2.76 | 0 | 0 | 0 | 2.76 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 1 | 0 | 1
LV Bkr Close | 0 | 0 | 40 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 2.76 | 0 | 0 | 0 | 2.76 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 25 | 0
LV SWGR | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 10 | 10 | 10 | [8 empty] | 3 | 3 | 3 | 3
UPS | 334 | 334 | 250 | 400 | 320 | 320 | 0 | 320 |  |  |  |  | 383.18 | 383.18 | 383.18 | 383.18 | 363.6 | 363.6 | 363.6 | 363.6 | 256 | 256 | 256 | 256 | 321 | 321 | 321 | 321 | 352 | 352 | 352 | 352 | 150 | 150 | 150 | 150
Fire Protection Panel | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Switchyard Relay Panel | [8 empty] | 150 | 25 | 100 | 25 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5
Feeder to Switchyard | [28 empty] | 100 | 10 | 100 | 10
Lock Out Relay | [16 empty] | 5 | 0 | 0 | 0 | 4.6 | 0 | 0 | 0 |  |  |  |  | 4.63 | 0 | 0 | 0
GCB Trip |  |  |  |  | 25.2 | 0 | 0 | 0 | [12 empty] | 6.1 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 12.6 | 0 | 0 | 0
GCB Close |  |  |  |  | 0 | 0 | 5 | 0 | [12 empty] | 0 | 0 | 2.3 | 0 |  |  |  |  | 0 | 0 | 2.3 | 0
GCB Charging Motor |  |  |  |  | 0 | 0 | 8 | 0 | [12 empty] | 0 | 0 | 4 | 0 |  |  |  |  | Assumed charge after close
Relay and Metering Panel |  |  |  |  | 6 | 6 | 6 | 6 | 10 | 10 | 10 | 10 | [8 empty] | 2 | 2 | 2 | 2 | [8 empty] | 10 | 10 | 10 | 10
DCS Cabinet |  |  |  |  | 20 | 20 | 0 | 20 | 10 | 10 | 10 | 10 | [16 empty] | 39 | 39 | 39 | 39 | 10 | 10 | 10 | 10
PLC |  |  |  |  | 0 | 0 | 0 | 0 | [24 empty] | 2 | 2 | 2 | 2
Emerg. Diesel Gen Control Pnl & 480V Bkr | [32 empty] | 1 | 5 | 5 | 1
THOROLD - STG - Siemens
Emergency Lube Oil Pump | 440 | 88 | 0 | 0
Power Supply for AVR | 16 | 16 | 16 | 16
Power Supply for Cabinet CJJ10 | 8 | 8 | 8 | 8
BARTOW - STG - Mitsubishi
ST Generator Regulation Panel (S-TGR) | [8 empty] | 10 | 10 | 10 | 10
STG Package Lighting | [8 empty] | 15 | 15 | 15 | 15
Turbine Protection Panel (S-TPR) | [8 empty] | 30 | 30 | 30 | 30
Generator Protection Panel (S-GPR) | [8 empty] | 15 | 15 | 15 | 15
STG DCS cabinets (S-DCS) | [8 empty] | 35 | 35 | 35 | 35
125VDC Motor Control Center (S-DMS) | [8 empty] | 296 | 296 | 0 | 0
STG Ventilation Valve | [8 empty] | 62 |  | 62 | 0
HINES 3 SWPC - STG
STG TXP Cabinet Feed 1 | [12 empty] | 10 | 10 | 10 | 10
STG TXP Cabinet Feed 2 | [12 empty] | 10 | 10 | 10 | 10
STG TXP Cabinet Feed 3 | [12 empty] | 8 | 8 | 8 | 8
STG TXP Cabinet Feed 4 | [12 empty] | 8 | 8 | 8 | 8
STG Generator Protective Panel (GPR) Feed 1 | [12 empty] | 10 | 10 | 10 | 10
STG Generator Protective Panel (GPR) Feed 2 | [12 empty] | 10 | 10 | 10 | 10
STG Auxiliary Protective Realy Panel (APR) | [12 empty] | 10 | 10 | 10 | 10
STG Voltage Regulator Cabinet/Panel Feed (AVR/VRP) | [12 empty] | 10 | 10 | 10 | 10
STG Emergency Lube Oil Pump 16kW (1 hour) | [12 empty] | 615 | 128 | 0 | 0
HINES 4 - STG
STG Emergency Lube Oil Pump 40hp (2 hour) | [16 empty] | 875 | 275 | 0 | 0
STG MARK VI (1FEED) | [16 empty] | 7 | 7 | 7 | 7
STG GPP (6 FEEDS)/EXCITER (1 FEED) | [16 empty] | 10 | 10 | 10 | 10
Palomar - STG - GE D11
Steam Turbine (ST) Emergency Lube Oil Pump | [20 empty] | 880 | 176 | 0 | 0
Steam Turbine (ST) Emergency Seal Oil Pump | [20 empty] | 710 | 142 | 0 | 0
ST Generator Protection Panel | [20 empty] | 24 | 24 | 24 | 24
ST Generator Mark VI control panel | [20 empty] | 7 | 7 | 7 | 7
GDMEC - STG
Steam Turbine (ST) Emergency Lube Oil Pump | [24 empty] | 820 | 230 | 0 | 0
Steam Turbine (ST) Emergency Seal Oil Pump | [24 empty] | 130 | 37 | 0 | 0
Generator Control Panel | [24 empty] | 10 | 10 | 10 | 10
TSI Cabinet | [24 empty] | 10 | 10 | 10 | 10
EHC Cabinet | [24 empty] | 24 | 24 | 24 | 24
Excitation Control Cubicle (AVR) | [24 empty] | 8 | 8 | 8 | 8
Generator Protection Relay Panel | [24 empty] | 10 | 10 | 10 | 10
FCB Cubicle | [24 empty] | 4 | 4 | 4 | 4
Excitation Cubicle Initial Excitation Control Pwr | [24 empty] | 8 | 8 | 8 | 8
Haynes - STG - GE D11
STG EB/SO PUMP (2hr Min) | [28 empty] | 825 | 275 | 0 | 0
STG Generator Protection Panel | [28 empty] | 20 | 2 | 2 | 2
STG 8 Generator Excitation Panel | [28 empty] | 3 | 3 | 3 | 3
STG 8 Generator Synchronizing Panel | [28 empty] | 3 | 3 | 3 | 3
STG 8 Trip Solenoid for ETD-1 | [28 empty] | 1 | 1 | 1 | 1
STG 8 Trip Solenoid for ETD-2 | [28 empty] | 1 | 1 | 1 | 1
STG 8 Trip Solenoid for ETD-3 | [28 empty] | 1 | 1 | 1 | 1
DPPP - FUJI STG
Turbine Generator Regulation Panel (S-TGR) | [32 empty] | 10 | 10 | 10 | 10
Thyristor (THY) | [32 empty] | 15 | 15 | 15 | 15
Turbine Protection Panel (S-TPR) | [32 empty] | 30 | 30 | 30 | 30
Generator Protection Panel (S-GPR) | [32 empty] | 15 | 15 | 15 | 15
STG DCS cabinets (S-DCS) | [32 empty] | 35 | 35 | 35 | 35
125VDC Motor Control Center (S-DMS) | [32 empty] | 206 | 82 | 2 | 2
Note on AH14: Note: Assumed 50% load.

## UPS Rollup (hidden)
Amps (per unit)
Description | Thorold | Panoche | Bartow | Hines 3 | Hines 4 | Palomar | GDMEC | Haynes
DCS Cabinet | 7.5 | 10 |  | 7.6 | 5.7 | 7.83 | 55.4
Communication System / Telephone | 1 | 10 |  | 5 | 5 | 14.71 | 14.71
Solenoid Valves | 2 | 6.6 |  | 6.6 | 6.6 |  |  | 20
Server |  |  |  | 7.24
OWS | 6 | 5 |  | 5.6 | 3 | 6.37 | 12.82 | 4.28
DB Server |  |  |  | 4.6 | 12
EWS | 6 | 5 |  | 4.6 | 3 | 3.43 |  | 2.91
HWS | 2 | 5 |  | 6 | 6 | 9.8 |  | 11.03
AMS Workstation |  |  |  | 7.24 | 3
Printer | 5 | 4 |  | 3 | 4 | 3.92 | 3.92
Color Printer |  |  |  | 1 | 0.6
Network Cabinet | 4 | 3 |  | 3 | 3 |  |  | 3
LP Drum Remote Level Element (Eye-Hi) | 0.5 |  |  | 0.5 | 0.5 |  |  | 1.96
IP Drum Remote Level Element (Eye-Hi) | 0.5 |  |  | 0.5 | 0.5
HP Drum Remote Level Element (Eye-Hi) | 0.5 |  |  | 0.5 | 0.5
Drum Water Level Gauge Control Panel | 8 |  |  |  | 8.82 | 6.71 |  | 2.12
Fire Alarm Panel | [7 empty] | 3.53
Ethernet Switches | [7 empty] | 1.18
HRSG Burner Mgmt System | [7 empty] | 6.21
STG TXP Cabinet |  |  |  | 10
SWPC CCR OT1 |  |  |  | 7.24
SWPC CCR DT 2 |  |  |  | 7.24
SWPC CCR ES680 |  |  |  | 7.24
SWPC CRY |  |  |  | 10
CTG 3A TXP (Primary CJQ01) |  |  |  | 10
CTG 3A Econopac Desk (CRX02) |  |  |  | 10
CEMS Log Printer | 3 | 3 |  | 3 | 4
CEMS OWS | 6 |  |  | 7.24 | 7 |  |  | 4.25
CEMS Power | 18 | 18 | 20 | 25 | 18 | 34.31 |  | 49.01
STG Mark VI | 15 |  |  |  | 10 | 20.7 |  | 16.67
STG Hydrogen Monitor Cabinet |  |  |  |  | 3.92 | 5.59 |  | 1.67
GE Local CTG Workstation | [7 empty] | 7
GE CTG Workstation |  | 10 |  |  | 7 | 9.83 |  | 2.91
GE STG Workstation | 7 |  | 5 |  | 7 | 2.01 |  | 2.91
GE CTG |  |  |  |  | 24
GE Ethernet | [5 empty] | 2 |  | 1
PLC/Control System | 2 | 10 |  |  |  | 9.8 | 9.8
PEECC Workstation
LEC Workstation
EHC Cubicle | [6 empty] | 29.41
TSI Cubicle | [6 empty] | 14.71

## Thorold (hidden)
Plant Battery Calculation Worksheet | [7 empty] | Plant UPS Calculation Worksheet
Thorold Cogeneration Project | [7 empty] | Thorold Cogeneration Project
2007-038 | [7 empty] | 2007-038
Plant Battery Voltage | 125 |  | Elapsed Time (minutes) | 1 | 60 | 239 | 240 | Plant UPS Voltage | 120 | Efficiency |  |  | 88%
Margin | 10% |  | Duration (minutes) | 1 | 59 | 179 | 1 | Margin | 25% | Single Phase
SERVICE | QUANTITY | RUN AMPS | NORMAL AMPS | DUTY CYCLE AMPS |  |  |  | SERVICE | QUANTITY | AMPS | KVA | Demand | Demand KVA
Steam Turbine | [7 empty] | Steam Turbine
Emergency Lube Oil Pump | 1 | 88 | 0 | 440 | 88 | 0 | 0 | Mark VI Control Panel | 1 | 15 | 1.8 | 0.95 | 1.71
Power Supply for AVR | 1 | 16 | 16 | 16 | 16 | 16 | 16 | Workstation | 1 | 7 | 0.84 | 0.7 | 0.588
Power Supply for Cabinet CJJ10 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | HRSG
Control System | [7 empty] | LP Drum Remote Level Element | 1 | 0.5 | 0.06 | 0.95 | 0.057
Misc Control Panels | 3 | 5 | 15 | 15 | 15 | 15 | 15 | IP Drum Remote Level Element | 1 | 0.5 | 0.06 | 0.95 | 0.057
Control Room Equipment | 3 | 10 | 30 | 30 | 30 | 30 | 30 | HP Drum Remote Level Element | 1 | 0.5 | 0.06 | 0.95 | 0.057
Electrically Operated Breakers | [7 empty] | Drum Water Level Gauge Control Panel | 3 | 8 | 2.88 | 0.95 | 2.736
Medium Voltage Breaker (Trip Coil A) | 6 | 10 | 0 | 60 | 0 | 0 | 0 | Control System
Medium Voltage Breaker (Trip Coil B) | 6 | 10 | 0 | 60 | 0 | 0 | 0 | DCS Cabinets | 8 | 7.5 | 7.2 | 0.95 | 6.84
Medium Voltage Breaker (Close) | 6 | 12 | 0 | 0 | 0 | 0 | 72 | Workstations | 10 | 6 | 7.2 | 0.4 | 2.88
Medium Voltage Switchgear (Normal) | 2 | 5 | 10 | 10 | 10 | 10 | 10 | Historian Workstation/Server | 1 | 6 | 0.72 | 0.4 | 0.288
Low Voltage Breaker (Trip) | 4 | 3 | 0 | 12 | 0 | 0 | 0 | LCD Monitors | 14 | 2 | 3.36 | 0.4 | 1.344
Low Voltage Breaker (Close) | 4 | 10 | 0 | 0 | 0 | 0 | 40 | Printers | 6 | 5 | 3.6 | 0.25 | 0.9
Low Voltage Switchgear (Normal) | 2 | 3 | 6 | 6 | 6 | 6 | 6 | Network Cabinet | 3 | 4 | 1.44 | 0.95 | 1.368
Misc. | [7 empty] | PLCs | 6 | 2 | 1.44 | 0.95 | 1.368
UPS | 1 | 333.69 | 400 | 333.69 | 333.69 | 333.69 | 250.2675 | Misc.
Fire Panel | 5 | 5 | 25 | 25 | 25 | 25 | 25 | Solenoid Valves | 45 | 2 | 10.8 | 0.05 | 0.54
| Total Load |  | 510 | 1015.69 | 531.69 | 443.69 | 472.2675 | CEMS Power | 4 | 18 | 8.64 | 0.95 | 8.208
| Plus 10% Margin |  | 51 | 101.569 | 53.169 | 44.369 | 47.2267 | CEMS Log Printer | 1 | 3 | 0.36 | 0.25 | 0.09
| Size Battery For |  | 561 | 1117.259 | 584.859 | 488.059 | 519.4942 | CEMS OWS | 1 | 6 | 0.72 | 0.4 | 0.288
Battery Charger Calculation | [7 empty] | Communications/Telephone | 15 | 1 | 1.8 | 0.25 | 0.45
Recharging Time (hours) | 12 |  | Amp-Hour Ratings |  |  |  |  | CTG Control Cabinet | 1 | 30 | 3.6 | 1 | 3.6
Minimum Battery Charger Capacity (A) | 732.5361 |  | 561 | 18.621 | 575.1113 | 1456.0427 | 8.6582
|  |  | Total Amp-Hour Rating (Ah) |  |  |  | 2058.4333 |  | KVA | Demand KVA
[8 empty] | Total Load | 56.58 | 33.369
[8 empty] | Efficiency 88% | 64.2955 | 37.9193
[8 empty] | Plus 25% Margin | 16.0739 | 9.4798
[8 empty] | Totals | 80.3693 | 47.3991
[8 empty] | UPS Chosen | 50 | KVA |  |  |  | 45
Note on L12: Note: Quantity of HRSGs.
Note on B13: Note: Quantity of 1 is Normal
Note on B14: Note: Quantity of 1 unless fed from UPS which is typical
Note on L15: Note: Zero out if there are no HRSGs on the project.
Note on B16: Note: Insert Number of Main Breakers
Note on B17: Note: Insert Number of Main Breakers
Note on B19: Note: Insert Number of Lineups
Note on B20: Note: Insert Number of Main Breakers
Note on B22: Note: Insert Number of Lineups
Note on C24: Note: UPS KVA value from UPS Calc Sheet.
Note on B25: Note: Haynes had 4.

## Panoche (hidden)
Battery Calculation Worksheet | [9 empty] | UPS Calculation Worksheet
Panoche Energy Center | [9 empty] | Panoche Energy Project
2007-018 | [9 empty] | 2007-018
Plant Battery Voltage | 125 |  | Elapsed Time (minutes) | 1 | 60 | 120 | 239 | 240 |  | Plant UPS Voltage | 120 | Efficiency |  |  | 88%
Margin | 10% |  | Duration (minutes) | 1 | 59 | 60 | 119 | 1 |  | Margin | 10% | Single Phase
SERVICE | QUANTITY | RUN AMPS | NORMAL AMPS | DUTY CYCLE AMPS | [5 empty] | SERVICE | QUANTITY | AMPS | KVA | Demand | Demand KVA
Relay Panels | [9 empty] | Combustion Turbine
Lock Out Relay for Generator and Breaker | 4 | 4.63 | 0 | 18.52 | 0 | 0 | 0 | 0 |  | Workstation | 4 | 10 | 4.8 | 0.7 | 3.36
Relay and Metering Panels | 3 | 2 | 6 | 6 | 6 | 6 | 6 | 6 |  |  |  |  | 0 | 1 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1 | 0
Control System | [9 empty] | HRSG
Misc Control Panels | 1 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | LP Drum Remote Level Element | 0 | 0.5 | 0 | 0.95 | 0
Control Room Equipment | 1 | 10 | 10 | 10 | 10 | 0 | 0 | 0 |  | IP Drum Remote Level Element | 0 | 0.5 | 0 | 0.95 | 0
DCS Cabinet | 2 | 10 | 20 | 20 | 20 | 0 | 0 | 0 |  | HP Drum Remote Level Element | 0 | 0.5 | 0 | 0.95 | 0
PLC | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | Drum Water Level Gauge Control Panel | 0 | 8 | 0 | 0.95 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1 | 0
Electrically Operated Breakers | [9 empty] | Control System
Medium Voltage Breaker (Trip) | 2 | 10 | 0 | 20 | 0 | 0 | 0 | 0 |  | DCS Cabinets | 2 | 10 | 2.4 | 0.95 | 2.28
Medium Voltage Breaker (Close) | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 24 |  | Engineering Workstation | 1 | 5 | 0.6 | 0.4 | 0.24
Medium Voltage Switchgear/MCC's (Normal) | 3 | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 91 | Historian Workstation/Server | 1 | 5 | 0.6 | 0.4 | 0.24
Low Voltage Breaker (Trip) | 2 | 3 | 0 | 6 | 0 | 0 | 0 | 0 | 69 | Operator Workstation | 6 | 5 | 3.6 | 0.7 | 2.52
Low Voltage Breaker (Close) | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 20 |  | Printer | 2 | 4 | 0.96 | 0.25 | 0.24
Low Voltage Switchgear (Normal) | 2 | 3 | 6 | 6 | 6 | 6 | 6 | 6 |  | Network Cabinet | 1 | 3 | 0.36 | 0.95 | 0.342
Generator Circuit Breaker (Trip) | 2 | 12.6 | 0 | 25.2 | 0 | 0 | 0 | 0 |  | PLCs | 2 | 10 | 2.4 | 0.95 | 2.28
Generator Circuit Breaker (Close) | 2 | 2.3 | 0 | 0 | 0 | 0 | 0 | 4.6 |  |  |  |  | 0 | 1 | 0
Generator Circuit Breaker (Charging Motor) | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 8 |  | Misc.
|  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Solenoid Valves | 5 | 6.6 | 3.96 | 0.05 | 0.198
Transformers | [9 empty] | CEMS Power | 4 | 18 | 8.64 | 0.95 | 8.208
Generator Step-Up Transformer Relay | 8 | 1 | 8 | 8 | 8 | 8 | 8 | 8 |  | CEMS Log Printer | 1 | 3 | 0.36 | 0.25 | 0.09
Unit Auxiliary Transformer Relay | 4 | 1 | 4 | 4 | 4 | 4 | 4 | 4 |  | CEMS OWS | 0 | 6 | 0 | 0.4 | 0
|  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Communications/Telephone | 1 | 10 | 1.2 | 0.5 | 0.6
Misc. | [12 empty] | 0 | 1 | 0
UPS | 1 | 320 | 320 | 320 | 320 | 160 | 0 | 0
Fire Panel | 14 | 2 | 28 | 28 | 28 | 28 | 28 | 28 |  |  | KVA | Demand KVA
|  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | Total Load | 29.88 | 20.598
| Total Load |  | 422 | 491.72 | 422 | 232 | 72 | 128.6 |  | Efficiency 88% | 33.9545 | 23.4068
| Plus 10% Margin |  | 42.2 | 49.172 | 42.2 | 23.2 | 7.2 | 12.86 |  | Plus 10% Margin | 3.3955 | 2.3407
| Size Battery For |  | 464.2 | 540.892 | 464.2 | 255.2 | 79.2 | 141.46 |  | Totals | 37.35 | 25.7475
Battery Charger Calculation | [9 empty] | UPS Chosen | 40 | KVA |  |  |  | Other
Recharging Time (hours) | 24 |  | Amp-Hour Ratings
Minimum Battery Charger Capacity (A) | 500.8715 |  | 464.2 | 9.0149 | 456.4633 | 255.2 | 157.08 | 2.3577
Rated Battery Charger Capacity (A) | 550 |  | Total Amp-Hour Rating (Ah) |  |  |  |  | 880.1159
Note on B9: Note: Number of Generators
Note on N9: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on B13: Note: Quantity of 1 is Normal
Note on M13: Note: Quantity of HRSGs.
Note on B14: Note: Quantity of 1 unless fed from UPS which is typical
Note on B15: Note: Number of DCS cabinet locations (typically 4 for a 2x1) (typically fed from UPS)
Note on B16: Note: Typically fed from UPS
Note on M16: Note: Zero out if there are no HRSGs on the project.
Note on B19: Note: Insert Number of Main Breakers
Note on N19: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on N20: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on B21: Note: Insert Number of Lineups
Note on N21: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on B22: Note: Insert Number of Main Breakers
Note on N22: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on B24: Note: Insert Number of Lineups
Note on N25: DPMcEnaney: Changed from original per Jeremy Buchanan
Note on B30: Note: Insert Number of GSUs
Note on B31: Note: Insert Number of UATs
Note on C34: Note: UPS KVA value from UPS Calc Sheet.
Note on B35: Note: Haynes had 4.

## Bartow (hidden)
Bartow Battery Calc | [11 empty] | Bartow UPS Calc
Data from: | Description | Quantity | Batteries |  | Duty1 | Minute | [5 empty] | Data from: | Description | Quantity | Inverter |  | Duty1
|  |  | Amps Each @ 125VDC | Total Amps |  | 1 | 2 - 120 | 121 - 179 | 180 | Continuous |  |  |  |  | Amps Each @ 120VAC | Total Amps
Mitsubishi1 | ST Emergency oil pump | 1 | 296 | 296 | PI, PS | 296 | 296 | 0 | 0 | 0 |  | Mitsubishi1 | ST Control Panel | 1 | 30 | 30 | C
Mitsubishi1 | ST Vacuum breaker | 1 | 1.2 | 1.2 | SI | 1.2 | 0 | 0 | 1.2 | 0 |  | Mitsubishi1 | ST Engineering Maintenance Station | 1 | 5 | 5 | C
Mitsubishi1 | ST Ventilation valve | 1 | 62.4 | 62.4 | PS | 62.4 | 0 | 0 | 62.4 | 0 |  | Mitsubishi1 | ST Generator control panel | 1 | 8.33 | 8.33 | C
Mitsubishi1 | ST package lighting | 1 | 12 | 12 | C | 12 | 12 | 12 | 12 | 0 |  | Mitsubishi1 | ST AVR cubicle (control panel) | 1 | 8.33 | 8.33 | C
Mitsubishi1 | ST control panel | 1 | 28.8 | 28.8 | C | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 |  | Mitsubishi1 | ST Generator Auxilary panel | 1 | 4.17 | 4.17 | C
Mitsubishi1 | ST generator emergency seal oil pump motor | 1 | 60 | 60 | I | 60 | 60 | 0 | 0 | 0 |  | Mitsubishi1 | ST Gas and seal oil control panel | 1 | 4.17 | 4.17 | I
Mitsubishi1 | ST Generator control panel | 1 | 4 | 4 | C | 4 | 4 | 4 | 4 | 4 |  | Assumptions | CEMS | 4 | 20 | 80 | C
Mitsubishi1 | ST AVR cubicle (control panel) | 1 | 16 | 16 | C | 16 | 16 | 16 | 16 | 16 |  | Assumptions | HRSG | 4 | 10 | 40 | C
Mitsubishi1 | ST Generator Auxiliary panel | 1 | 6.4 | 6.4 | C | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 |  | Assumptions | Miscellaneous Control Room Equipment | 1 | 40 | 40 | C
Mitsubishi1 | ST Generator Protection panel | 1 | 4 | 4 | C | 4 | 4 | 4 | 4 | 4 |  | Assumptions | Miscellaneous Plant Equipment | 1 | 50 | 50 | C
Mitsubishi1 | ST Gas and seal oil control panel | 1 | 4 | 4 | PC | 4 | 4 | 4 | 4 | 4 |  | Continuous load |  |  |  | 270
Assumptions | DCS Cabinets | 6 | 10 | 60 | C | 60 | 60 | 60 | 60 | 60 |  | 125% of continuous load |  |  |  | 337.5
Assumptions | 5kV breakers (trip - first minute) | 9 | 14 | 126 | PS | 126 | 0 | 0 | 0 | 0
Assumptions | 5kV breakers (close - last minute) | 9 | 10 | 90 | PS | 0 | 0 | 0 | 90 | 0
Assumptions | 480V SUS Breakers (trip - first minute) | 4 | 9 | 36 | PS | 36 | 0 | 0 | 0 | 0 |  | Design Criteria | Inverter sizing factor | 125% of continuous load
Assumptions | 480V SUS Breakers (close - last minute) | 4 | 9 | 36 | PS | 0 | 0 | 0 | 36 | 0 |  | Design Criteria | AC bus (output) voltage | 120VAC
Assumptions | DC Panel - 245kV breakers | 1 | 25 | 25 | C | 150 | 25 | 25 | 100 | 25 |  | Design Criteria | DC bus (input) voltage | 125VDC
UPS calculation | 45kVA Inverter2 | 1 | 162 | 162 | C | 162 | 162 | 162 | 162 | 162
Assumptions | GSUs | 5 | 5 | 25 | C | 25 | 25 | 25 | 25 | 25
Assumptions | Auxiliary Transformers | 4 | 5 | 20 | C | 20 | 20 | 20 | 20 | 20 |  | ***Inverter size calculations***
Assumptions | 4160V SWGR / MCCs and 480V SUSs | 1 | 10 | 10 | C | 10 | 10 | 10 | 10 | 10 |  | Power Factor |  |  | 1
Assumptions | KPE Relay Panel | 1 | 10 | 10 | C | 10 | 10 | 10 | 10 | 10 |  | Inverter efficiency3 |  |  | 0.8
Totals |  |  |  | 1094.8 |  | 1093.8 | 743.2 | 387.2 | 651.8 | 375.2 |  | Inverter size in kVA needed for continuous load (125% of continuous load * 120VAC) |  |  | 40500 | kVA | (Output kVA)
Totals + 10% Design Margin + 1.25 Aging Factor | [5 empty] | 1476.63 | 1003.32 | 522.72 | 879.93 |  |  | Inverter size in kW needed for continuous load (125% of continuous load kVA * PF) |  |  | 40500 | kW | (Output kW)
[12 empty] | Input power required from the DC bus (Output kW / Inverter Efficiency) |  |  | 50625 | kW | (Input kW)
[12 empty] | Input amps required from the DC bus (Input kW / 125VDC) |  |  | 405 | A | (Input A)
Calculations | 45kVA Inverter in emergency battery operation2 | 162 | A | ***Battery Amp-hour calculations (this includes the 10% design margin and the 1.25 aging factor)*** | [7 empty] | Recommended Fuse Size (Already sized for 125% load using calculation above) |  | > | 405 | A
Design Criteria | Design Margin (assumed for batteries and charger) | 10% |  |  | A-hr | 24.6105 | 1989.918 | 514.008 | 14.6655 |  |  | Recommended inverter size |  | > | 40.5 | kVA | (Output kVA rating)
Design Criteria | Aging Factor | 1.25 |  |  | Total Battery A-hr |  |  |  | 2543.202 | A-hr
Design Criteria | AC bus | 120VAC | [9 empty] | Emergency battery operation amperage draw2 |  |  | 162 | A | (Input A)
Design Criteria | DC bus | 125VDC
***Battery Charger Amp-hour Calculations (calculated from the total load)***
[5 empty] | A-hr | 18.23 | 1474.0133 | 380.7467 | 10.8633 |  |  | ***Notes***
[5 empty] | Total Battery Charger A-hr |  |  |  | 1883.8533 | A-hr |  | 1 Mitsubishi submittal, "Electrical Load List 202-ED-0011-01 - Bartow Repowering Project 2006011 - 04/18/2006 - INF"
2 For emergency battery operation, figure for 50% of the continuous load, the power factor, and the inverter efficiency.
[5 empty] | Ampere-hours of emergency discharge |  |  |  | C | 1883.8533 | A-h | 3 Actual Spec: 80 - 94% from GUTOR, technical data sheets, AC UPS system PDW 3000, 10 - 220-kVA Three Phase
[5 empty] | Continuous load |  |  |  | L | 375.2 | A
***Notes*** |  |  |  |  | Hours of recharge time |  |  |  | H | 12 | hr
1 Electrical Load List 202-ED-0011-01 - Bartow Repowering Project 2006011 - 04/18/2006 - INF |  |  |  |  | Lead-Acid Cell Recharge Inefficiency3 |  |  |  |  | 1.1
2 From the emergency battery operation amperage draw calculated on the "Bartow UPS Sizing and Equipment List"
3 Assumed efficiency |  |  |  |  | Ampere Charger = L + (1.1 * C) / L
[5 empty] | Ampere Charger (A) > |  | 547.8866 | A
[5 empty] | Recommended Ampere Charger |  |  | 600A

## Hines 3 (hidden)
125VDC AMPS REQUIRED DURING A LOSE OF STATION POWER | [5 empty] | STG ENCLOSURE UPS PANEL
Equipment and Amps need per period | Duty Cycle (180 minutes) |  |  |  |  | Service | VAC | A | VA | PF | W
| 1 | 59 | 59 | 1 | 60 | 5kV PDC DCS Cabinet | 120 | 6.5 | 780 | 0.85 | 663
CTG 3A Generator Circuit Breaker Close Coil | 0 | 0 | 0 | 3.8 | 0 | STG PDC DCS Cabinet | 120 | 8.89 | 1067 | 0.85 | 907
CTG 3A Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | 0 | CW Intake DCS Cabinet | 120 | 2.18 | 262 | 0.85 | 222
CTG 3A Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | 0 | Control Room UPS Panel | 120 | 114.68 | 13762 |  | 11697
CTG 3B Generator Circuit Breaker Close Coil | 0 | 0 | 0 | 3.8 | 0 | HRSG 3A Enclosure UPS Panel | 120 | 61.93 | 7432 |  | 5984
CTG 3B Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | 0 | HRSG 3B Enclosure UPS Panel | 120 | 61.93 | 7432 |  | 5984
CTG 3B Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | 0 | Communication System Feed 1 | 120 | 5 | 600 | 0.85 | 510
CTG 3S Generator Circuit Breaker Close Coil | 0 | 0 | 0 | 3.8 | 0 | Communication System Feed 2 | 120 | 5 | 600 | 0.85 | 510
CTG 3S Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | 0 | Communication System Feed 3 | 120 | 5 | 600 | 0.85 | 510
CTG 3S Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | 0 | Communication System Feed 4 | 120 | 5 | 600 | 0.85 | 510
CTG 3A Generator Step-Up Transformer | 10 | 10 | 10 | 10 | 0 | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 341
CTG 3B Generator Step-Up Transformer | 10 | 10 | 10 | 10 | 0 | STG TXP Cabinet | 120 | 10 | 1200 | 0.85 | 1020
CTG 3S Generator Step-Up Transformer | 10 | 10 | 10 | 10 | 0 | Total |  | 292.71 | 35125 |  | 28859
Unit Auxiliary Transformer 3 | 10 | 10 | 10 | 10 | 0
Unit Auxiliary Transformer 4 | 10 | 10 | 10 | 10 | 0 | CONTROL ROOM UPS PANEL
4160V Circuit Breaker 3A Close Coil | 7 | 0 | 0 | 7 | 0 | Service | VAC | A | VA | PF | W
4160V Circuit Breaker 3B Close Coil | 7 | 0 | 0 | 7 | 0 | OPC Server 1 | 120 | 7.24 | 869 | 0.85 | 738
4160V Switchgear/Motor Control Centers | 10 | 10 | 10 | 10 | 0 | OPC Server 2 | 120 | 7.24 | 869 | 0.85 | 738
480V SUS Circuit Breaker 3A | 2.76 | 0 | 0 | 2.76 | 0 | OWS 1 | 120 | 5.6 | 672 | 0.85 | 571
480V SUS Circuit Breaker 3B | 2.76 | 0 | 0 | 2.76 | 0 | OWS 2 | 120 | 5.6 | 672 | 0.85 | 571
UPS System (40kVA) | 383.18 | 383.18 | 383.18 | 383.18 | 383.18 | OWS 3 | 120 | 5.6 | 672 | 0.85 | 571
Fire Protection Panel | 10 | 10 | 10 | 10 | 0 | DB Server | 120 | 4.6 | 552 | 0.85 | 469
STG Emergency Lube Oil Pump 16kW (1 hour) | 615 | 128 | 0 | 0 | 0 | EWS | 120 | 4.6 | 552 | 0.85 | 469
STG Voltage Regulator Cabinet/Panel Feed (AVR/VRP) | 10 | 10 | 10 | 10 | 0 | HWS | 120 | 6 | 720 | 0.85 | 612
STG TXP Cabinet Feed 1 | 10 | 10 | 10 | 10 | 0 | AMS Workstation | 120 | 7.24 | 869 | 0.85 | 738
STG TXP Cabinet Feed 2 | 10 | 10 | 10 | 10 | 0 | HP5100 B/W LP 1 | 120 | 3 | 360 | 0.85 | 306
STG TXP Cabinet Feed 3 | 8 | 8 | 8 | 8 | 0 | HP5100 B/W LP 2 | 120 | 3 | 360 | 0.85 | 306
STG TXP Cabinet Feed 4 | 8 | 8 | 8 | 8 | 0 | HP5100 B/W LP 3 | 120 | 3 | 360 | 0.85 | 306
STG Generator Protective Panel (GPR) Feed 1 | 10 | 10 | 10 | 10 | 0 | HP5100 B/W LP 4 | 120 | 3 | 360 | 0.85 | 306
STG Generator Protective Panel (GPR) Feed 2 | 10 | 10 | 10 | 10 | 0 | HP2600 Color Printer | 120 | 1 | 120 | 0.85 | 102
STG Auxiliary Protective Realy Panel (APR) | 10 | 10 | 10 | 10 | 0 | Network Cabinet (Primary) | 120 | 3 | 360 | 0.85 | 306
Progress Energy Switchyard Relay Panel 1 | 10 | 10 | 10 | 10 | 0 | HRSG 3A LP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
Progress Energy Switchyard Relay Panel 2 | 10 | 10 | 10 | 10 | 0 | HRSG 3A IP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
Total Load | 1270.1 | 677.18 | 549.18 | 580.1 | 383.18 | HRSG 3A HP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
Plus 10% Margin | 127.01 | 67.72 | 54.92 | 58.01 | 38.32 | HRSG 3B LP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
Size Battery For | 1397.11 | 744.9 | 604.1 | 638.11 | 421.5 | HRSG 3B IP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[6 empty] | HRSG 3B HP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[6 empty] | SWPC CCR OT1 | 120 | 7.24 | 869 | 0.85 | 738
[6 empty] | SWPC CCR DT 2 | 120 | 7.24 | 869 | 0.85 | 738
[6 empty] | SWPC CCR ES680 | 120 | 7.24 | 869 | 0.85 | 738
[6 empty] | SWPC CRY | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | CEMS Log Printer | 120 | 3 | 360 | 0.85 | 306
[6 empty] | CEMS OWS | 120 | 7.24 | 869 | 0.85 | 738
[6 empty] | Total |  | 114.68 | 13762 |  | 11697
HRSG 3A ENCLOSURE UPS PANEL
[6 empty] | Service | VAC | A | VA | PF | W
[6 empty] | HRSG 3A DCS Cabinet | 120 | 10.33 | 1240 | 0.85 | 1054
[6 empty] | CEMS 3A Power Strip Workbench Area | 120 | 5 | 600 | 0.85 | 510
[6 empty] | CEMS 3A Power Strip Spectrum Rack 1 | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | CEMS 3A Power Strip Spectrum Rack 2 | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 341
[6 empty] | CTG 3A TXP (Primary CJQ01) | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | CTG 3A Econopac Desk (CRX02) | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | Total |  | 61.93 | 7432 |  | 5984
HRSG 3B ENCLOSURE UPS PANEL
[6 empty] | Service | VAC | A | VA | PF | W
[6 empty] | HRSG 3B DCS Cabinet | 120 | 10.33 | 1240 | 0.85 | 1054
[6 empty] | CEMS 3B Power Strip Workbench Area | 120 | 5 | 600 | 0.85 | 510
[6 empty] | CEMS 3B Power Strip Spectrum Rack 1 | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | CEMS 3B Power Strip Spectrum Rack 2 | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 341
[6 empty] | CTG 3B TXP (Primary CJQ01) | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | CTG 3B Econopac Desk (CRX02) | 120 | 10 | 1200 | 0.85 | 1020
[6 empty] | Total |  | 61.93 | 7432 |  | 5984

## Hines 4 (hidden)
125VDC AMPS REQUIRED DURING A LOSE OF STATION POWER |  |  |  |  | STG ENCLOSURE UPS PANEL
Equipment and Amps need per period | Duty Cycle (180 minutes) |  |  |  | Service | VAC | A | VA | PF | W
| 1 | 118 | 1 | 60 | 5KV ELECTRICAL EQUIPMENT ENCLOSURE DCS | 120 | 4 | 480 | 0.7 | 336
CTG 4A Generator Circuit Breaker Close Coil | 0 | 0 | 3.8 | 0 | STG ELECTRICAL EQUIPMENT ENCLOSURE DCS | 120 | 6.5 | 780 | 0.7 | 546
CTG 4A Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | CW INTAKE DCS | 120 | 2 | 240 | 0.7 | 168
CTG 4A Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | PNL-646-402 Control Room UPS Panel | 120 | 77.8 | 9336 |  | 7935.6
CTG 4B Generator Circuit Breaker Close Coil | 0 | 0 | 3.8 | 0 | PNL-646-403 HRSG 4A Enclosure UPS Panel | 120 | 65.42 | 7850.4 |  | 6340.2
CTG 4B Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | PNL-646-404 HRSG 4B Enclosure UPS Panel | 120 | 65.42 | 7850.4 |  | 6340.2
CTG 4B Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 340.56
CTG 4S Generator Circuit Breaker Close Coil | 0 | 0 | 3.8 | 0 | STG MARK VI | 120 | 10 | 1200 | 0.85 | 1020
CTG 4S Generator Circuit Breaker Trip Coil 1 | 14.4 | 0 | 0 | 0 | STG HYDROGEN MONITOR CABINET | 120 | 3.92 | 470.4 | 0.85 | 399.84
CTG 4S Generator Circuit Breaker Trip Coil 2 | 14.4 | 0 | 0 | 0 | Total |  | 241.66 | 27739.2 |  | 22544.4
CTG 4A Generator Step-Up Transformer | 4 | 4 | 4 | 0
CTG 4B Generator Step-Up Transformer | 4 | 4 | 4 | 0 | Total UPS amps = | 241.66 | A
CTG 4S Generator Step-Up Transformer | 4 | 4 | 4 | 0 | UPS DC to AC percent efficiency = | 88%
Unit Auxiliary Transformer 402 | 4 | 4 | 4 | 0 | UPS Design Margin = | 125%
4160V Circuit Breaker 4A Trip/Close Coil | 7 | 0 | 2 | 0 | Calculated UPS KVA = (120VAC x UPS amps x Design Margin)/1,000 = | 36.249 | KVA
4160V Circuit Breaker 4B Trip/Close Coil | 7 | 0 | 2 | 0 | Next Standard Manufacturer UPS Size = | 40 | KVA
LCI 4160V Circuit Breaker Trip | 7 | 0 | 0 | 0
LOCK OUT RELAYS (3) | 15 | 0 | 0 | 0 | DC Amps needed from Plant Battery:
4160V Switchgear/Motor Control Centers | 10 | 10 | 10 | 0 | VA = W @ 1.0PF = | 36249 | VA
480V SUS Circuit Breaker 4A | 2.76 | 0 | 2.76 | 0 | DC Amps = KW/(125VDC x 0.88) = | 329.5364 | A
480V SUS Circuit Breaker 4B | 2.76 | 0 | 2.76 | 0
UPS System (full load from UPS calc) | 363.6 | 363.6 | 363.6 | 363.6 | CONTROL ROOM UPS PANEL
Fire Protection Panel | 10 | 10 | 10 | 0 | Service | VAC | A | VA | PF | W
STG Emergency Lube Oil Pump 40hp (2 hour) | 875 | 275 | 275 | 0 | OWS 1 | 120 | 3 | 360 | 0.85 | 306
STG MARK VI (1FEED) | 7 | 7 | 7 | 0 | OWS 2 | 120 | 3 | 360 | 0.85 | 306
STG GPP (6 FEEDS)/EXCITER (1 FEED) | 10 | 10 | 10 | 0 | DB Server | 120 | 12 | 1440 | 0.85 | 1224
Progress Energy Switchyard Relay Panel 1 | 5 | 5 | 5 | 5 | EWS | 120 | 3 | 360 | 0.85 | 306
Progress Energy Switchyard Relay Panel 2 | 5 | 5 | 5 | 5 | HWS | 120 | 6 | 720 | 0.85 | 612
Total Load in AMPS | 1429.52 | 701.6 | 722.52 | 373.6 | AMS Workstation | 120 | 3 | 360 | 0.85 | 306
[5 empty] | HP5100 B/W LP 1 | 120 | 4 | 480 | 0.85 | 408
[5 empty] | HP5100 B/W LP 2 | 120 | 4 | 480 | 0.85 | 408
[5 empty] | HP2600 Color Printer | 120 | 0.6 | 72 | 0.85 | 61.2
[5 empty] | Network Cabinet (Primary) | 120 | 3 | 360 | 0.85 | 306
[5 empty] | Monitors that are not included with control room equip. | 120 | 3.2 | 384 | 0.85 | 326.4
[5 empty] | Communcation System | 120 | 5 | 600 | 0.85 | 510
[5 empty] | HRSG 4A LP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | HRSG 4A IP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | HRSG 4A HP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | HRSG 4B LP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | HRSG 4B IP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | HRSG 4B HP Drum Remote Level Element (Eye-Hi) | 120 | 0.5 | 60 | 0.85 | 51
[5 empty] | GE CTG(s) Workstation (dual monitors) | 120 | 7 | 840 | 0.85 | 714
[5 empty] | GE STG(s) Workstation (dual monitors) | 120 | 7 | 840 | 0.85 | 714
[5 empty] | CEMS Log Printer | 120 | 4 | 480 | 0.85 | 408
[5 empty] | CEMS OWS | 120 | 7 | 840 | 0.85 | 714
[5 empty] | Total |  | 77.8 | 9336 |  | 7935.6
HRSG 4A ENCLOSURE UPS PANEL
[5 empty] | Service | VAC | A | VA | PF | W
[5 empty] | HRSG 4A DCS Cabinet(s) | 120 | 8 | 960 | 0.85 | 816
[5 empty] | CEMS 4A Power | 120 | 18 | 2160 | 0.85 | 1836
[5 empty] | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 340.56
[5 empty] | Drum Water Level Gauge Control Panel (HP,IP,LP) | 120 | 8.82 | 1058.4 | 0.85 | 899.64
[5 empty] | CTG 4A | 120 | 24 | 2880 | 0.85 | 2448
[5 empty] | Total |  | 65.42 | 7850.4 |  | 6340.2
HRSG 4B ENCLOSURE UPS PANEL
[5 empty] | Service | VAC | A | VA | PF | W
[5 empty] | HRSG 4B DCS Cabinet(s) | 120 | 8 | 960 | 0.85 | 816
[5 empty] | CEMS 4B Power | 120 | 18 | 2160 | 0.85 | 1836
[5 empty] | Solenoid Valves | 120 | 6.6 | 792 | 0.43 | 340.56
[5 empty] | Drum Water Level Gauge Control Panel (HP,IP,LP) | 120 | 8.82 | 1058.4 | 0.85 | 899.64
[5 empty] | CTG 4B | 120 | 24 | 2880 | 0.85 | 2448
[5 empty] | Total |  | 65.42 | 7850.4 |  | 6340.2

## Palomar (hidden)
|  |  |  | AH1 | AH2 | AH3 | AH4 | AH5
DC Loads |  |  | Total Elapsed Time (minutes) | 1 | 60 | 120 | 179 | 180 | 5.3 UPS SIZING CALCULATION
|  |  | Duration (minutes) | 1 | 59 | 60 | 59 | 1
SERVICE | QUANTITY | LRA AMPS | RUN AMPS | [6 empty] | CONTROL ROOM
Steam Turbine (ST) Emergency Lube Oil Pump | 1 | 880 | 176 | 880 | 176 | 0 | 0 | 0 |  | Item | Quantity | Watts/Unit | Total Watts |  | AMPS
Steam Turbine (ST) Emergency Seal Oil Pump | 1 | 710 | 142 | 710 | 142 | 142 | 0 | 0 |  | CRT, 21" | 13 | 200 | 2600 |  | 1.9608
ST Generator Protection Panel | 1 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | Operator Stations | 8 | 250 | 2000 |  | 2.451
ST Generator Mark VI control panel | 1 |  | 7 | 7 | 7 | 7 | 7 | 7 |  | Engineering Stations | 2 | 350 | 700 |  | 3.4314
GSUs & UATs Buckholtz relays | 5 |  | 3 | 15 | 15 | 15 | 15 | 15 |  | Historian | 1 | 1000 | 1000 |  | 9.8039
CT GCBs Trip | 2 |  | 6.1 | 12.2 | 0 | 0 | 0 | 0 |  | Laser Printers (2 operating) | 5 | 400 | 800 |  | 3.9216
CT GCBs Close | 2 |  | 2.3 | 0 | 0 | 0 | 0 | 6.9 |  | GE Ethernet | 2 | 190 | 380 |  | 1.8627
CT GCBs Charging Motor | 2 |  | 4 | 0 | 0 | 0 | 0 | 8 |  | Misc Equipment | 1 | 1000 | 1000 |  | 9.8039
Lock out Relay for Generator and Breaker | 2 |  | 4.6 | 9.2 | 0 | 0 | 0 | 0
4.16 KV Breakers (Trip) | 2 |  | 7 | 14 | 0 | 0 | 0 | 0 |  |  |  |  | 8500 | watts
4.16 KV Breakers (Close) | 2 |  | 14 | 0 | 0 | 0 | 0 | 28
5kV SWGR/MCC Continuous Load | 2 |  | 5 | 10 | 10 | 10 | 10 | 10 |  | DCS ROOM
Clg Twr 5kV MCC Continuous Load | 1 |  | 5 | 5 | 5 | 5 | 5 | 5 |  | Item | Quantity | Watts/Unit | Total Watts
480V SUS Breakers (Trip) | 4 |  | 2 | 8 | 0 | 0 | 0 | 0 |  | DCS Cabinets | 1 | 2000 | 2000 |  | 19.6078
480V SUS Breakers (Close) | 4 |  | 8 | 0 | 0 | 0 | 0 | 32 |  | Telephone Equipment | 1 | 1500 | 1500 |  | 14.7059
480V SWGR Continuous Load | 2 |  | 3 | 6 | 6 | 6 | 6 | 6 |  | Misc Equipment | 1 | 1000 | 1000 |  | 9.8039
Misc Control Panels | 1 |  | 5 | 5 | 5 | 5 | 5 | 5
40 KVA UPS Inverter, 100% loaded, 0.8pf | 1 |  | 256 | 256 | 256 | 256 | 256 | 256 |  |  |  |  | 4500 | watts
Protective Relay and Metering Panels | 3 |  | 2 | 6 | 6 | 6 | 6 | 6
WATER TREATMENT DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
Bold numbers indicate continuous DC loads | TOTAL LOAD |  |  | 1967.4 | 652 | 476 | 334 | 408.9 |  | DCS Cabinet | 1 | 200 | 200 |  | 1.9608
| PLUS 10 % MARGIN |  |  | 196.74 | 65.2 | 47.6 | 33.4 | 40.89 |  | PLC/Control System | 1 | 1000 | 1000 |  | 9.8039
| SIZE BATTERY FOR |  |  | 2164.14 | 717.2 | 523.6 | 367.4 | 449.79 |  | Misc Equipment | 1 | 1000 | 1000 |  | 9.8039
[13 empty] | 2200 | watts
COOLING TOWER DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | DCS Cabinet | 1 | 300 | 300 |  | 2.9412
[13 empty] | 300 | watts
HRSG 1, STG DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | DCS Cabinet | 1 | 2000 | 2000 |  | 19.6078
[13 empty] | 2000 | watts
HRSG 2 DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | DCS Cabinet | 1 | 1500 | 1500 |  | 14.7059
[13 empty] | 1500 | watts
Switch Yard DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | DCS Cabinet | 1 | 300 | 300 |  | 2.9412
[13 empty] | 300 | watts
5kV SWGR BLDG DCS
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | DCS Cabinet | 1 | 500 | 500 |  | 4.902
[10 empty] | Misc Equipment | 1 | 1000 | 1000 |  | 9.8039
[13 empty] | 1500 | watts
CEMS Shelters
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | CEMS total UPS load | 2 | 3500 | 7000 |  | 34.3137
[13 empty] | 7000 | watts
CTG LOADs
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | PEECC HMI/Ethernet | 2 | 1003 | 2006 |  | 9.8333
[10 empty] | LEC HMI/Ethernet | 1 | 205 | 205 |  | 2.0098
[13 empty] | 2211 | watts
STG LOADs
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | Ethernet for GEC & Mark VI | 2 | 205 | 410 |  | 2.0098
[10 empty] | Hyd. Control Cabenit | 1 | 570 | 570 |  | 5.5882
[10 empty] | Mark VI | 1 | 2111 | 2111 |  | 20.6961
[13 empty] | 3254 | watts
HRSG LOADs
[10 empty] | Item | Quantity | Watts/Unit | Total Watts
[10 empty] | Drum Level Units | 2 | 684 | 1368 |  | 6.7059
[13 empty] | 1440 | watts
[9 empty] | TOTAL PLANT UPS WATTS |  |  |  | 34705 | watts
[10 empty] | Power Factor |  |  | 0.95
[9 empty] | UPS kVA |  |  |  | 36531 | kVA

## GDMEC (hidden)
|  |  | Total Elapsed Time (minutes) | 1 | 60 | 90 | 179 | 180 | 5.3 UPS SIZING CALCULATION
|  |  | Duration (minutes) | 1 | 59 | 30 | 89 | 1
SERVICE | QUANTITY | LRA AMPS | RUN AMPS | [6 empty] | CONTROL ROOM
Steam Turbine (ST) Emergency Lube Oil Pump | 1 | 820 | 230 | 820 | 230 | 0 | 0 | 0 |  |  | Quantity | Item | Watts/Unit | Total Watts
Steam Turbine (ST) Emergency Seal Oil Pump | 1 | 130 | 37 | 130 | 37 | 0 | 0 | 0 |  |  | 10 | CRT, 21" | 600 | 6000 |  | 5.8824
Generator Control Panel | 1 |  | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 6 | Personal Computers | 312 | 1872 |  | 3.0588
TSI Cabinet | 1 |  | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 5 | Laser Printers (2 operating) | 400 | 800 |  | 3.9216
EHC Cabinet | 1 |  | 24 | 24 | 24 | 24 | 24 | 24 |  |  | 1 | Misc Equipment | 1500 | 1500 |  | 14.7059
Excitation Control Cubicle (AVR) | 1 |  | 8 | 8 | 8 | 8 | 8 | 8
Generator Protection Relay Panel | 1 |  | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | CONTROL ROOM TOTALS |  | 10172 | watts
Initial Excitation Power | 1 |  | 120 | 0 | 0 | 0 | 0 | 0
FCB Cubicle | 1 |  | 4 | 4 | 4 | 4 | 0 | 0
Excitation Cubicle Initial Excitation Control Pwr | 1 |  | 8 | 8 | 8 | 8 | 0 | 0 |  | DCS ROOM
Generator Circuit Breakers | 2 |  | 7 | 14 | 0 | 0 | 0 | 0 |  |  | Quantity | Item | Watts/Unit | Total Watts
40 KVA UPS Inverter, 30KW UPS Load, 0.8PF | 1 |  | 320.8556 | 320.8556 | 320.8556 | 267.3797 | 267.3797 | 267.3797 |  |  | 2 | DCS Cabinets | 3453 | 7.028 |  | 33.8529
4.16 KV Breakers (Trip) | 5 |  | 7 | 35 | 0 | 0 | 0 | 0 |  |  | 1 | Telephone Equipment | 1500 | 1500 |  | 14.7059
4.16 KV Breakers (Close) | 2 |  | 5 | 0 | 0 | 0 | 0 | 10 |  |  | 1 | Misc Equipment | 1500 | 1500 |  | 14.7059
480V SUS Breakers (Trip) | 3 |  | 3 | 9 | 0 | 0 | 0 | 0
480V SUS Breakers (Close) | 1 |  | 3 | 0 | 0 | 0 | 0 | 3 |  |  |  | DCS ROOM TOTALS |  | 10028 | watts
Misc Control Panels | 1 |  | 5 | 5 | 5 | 5 | 5 | 5
| TOTAL LOAD |  |  | 1407.8556 | 666.8556 | 346.3797 | 334.3797 | 347.3797 |  | WATER TREATMENT DCS
| PLUS 15 % MARGIN |  |  | 211.1783 | 100.0283 | 51.957 | 50.157 | 52.107 |  |  | Quantity | Item | Watts/Unit | Total Watts
| SIZE BATTERY FOR |  |  | 1619.034 | 766.884 | 398.3366 | 384.5366 | 399.4866 |  |  | 0 | DCS Cabinet | 0 | 0 |  | 0
[11 empty] | 1 | PLC/Control System | 1000 | 1000 |  | 9.8039
[11 empty] | 1 | Misc Equipment | 1000 | 1000 |  | 9.8039
[12 empty] | WATER TREATMENT DCS TOTALS |  | 2000 | watts
COOLING TOWER DCS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 1 | DCS Cabinet | 3216 | 3216 |  | 31.5294
[12 empty] | COOLING TOWER DCS TOTALS |  | 3216 | watts
HRSG 1 (CEMS) DCS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 1 | DCS Cabinet | 3307 | 3307 |  | 32.4216
[12 empty] | HRSG 1 (CEMS) DCS TOTALS |  | 3307 | watts
HRSG 2 (CEMS) DCS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 1 | DCS Cabinet | 3321 | 3321 |  | 32.5588
[12 empty] | HRSG 2 (CEMS) DCS TOTALS |  | 3321 | watts
STG DCS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 1 | DCS Cabinet | 15024 | 15024 |  | 147.2941
[12 empty] | STG DCS TOTALS |  | 15024 | watts
5kV SWGR BLDG DCS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 0 | DCS Cabinet | 0 | 0 |  | 0
[11 empty] | 1 | Misc Equipment | 1500 | 1500 |  | 14.7059
[12 empty] | 4160V SWGR BLDG DCS TOTALS |  | 1500 | watts
STEAM TURBINE LOADS
[11 empty] | Quantity | Item | Watts/Unit | Total Watts
[11 empty] | 1 | EHC Cubicle | 3000 | 3000 |  | 29.4118
[11 empty] | 1 | TSI Cubicle | 1500 | 1500 |  | 14.7059
[12 empty] | Misc Loads | 1500 | 1500 |  | 14.7059
[12 empty] | STEAM TURBINE LOAD TOTALS |  | 6000 | watts
[10 empty] | SUM PLANT UPS TOTAL WATTS |  |  |  | 54.568 | watts
[10 empty] | (MISC LOADS) |  |  |  | -7000 | watts
[9 empty] | TOTAL PLANT UPS WATTS |  |  |  |  | 47568 | watts

## Haynes (hidden)
DC LOADS on 125 VDC System
| 1st Minute Transients + Continuous | Minutes 1 to 120 | Minutes 121 to 239 | Minute 239 to 240 - Continuous + Transient
LOR for ST Generator and Breaker | 4.63 |  |  |  | Electroswitch Series 24 LOR at 125VDC applied, 27 ohm resistance | 5.1 UPS SIZING CALCULATION
LOR for CT Generator and Breaker | 4.63
LOR for CT Generator and Breaker | 4.63 | [5 empty] | CONTROL ROOM
Electrically Operated Aux Main Breakers | [7 empty] | Quantity | Item | Watts/Unit | Total Watts
4160V Main Breaker 1 | 10.5 |  |  | 23 | MV breaker transient values. All values GE. |  |  | 8 | Operator WS CRT | 140 | 1120 |  | 1.3725
4160V Main Breaker 2 | 10.5 |  |  | 23 | Trip Coil current = 10.5 A (3 cycle breaker due to fast transfer) |  |  | 4 | Operator Work Stations | 157 | 628 |  | 1.5392
13.8kV Main Breaker 1 | 10.5 |  |  | 23 | Motor inrush = 23 A (charging motor engages after close) |  |  | 1 | Engineering WS CRT | 140 | 140 |  | 1.3725
13.8kV Main Breaker 2 | 10.5 |  |  | 23 | Motor windup = 8 A |  |  | 1 | Engineering Work Station | 157 | 157 |  | 1.5392
480V Switchgear Main Breaker 1 | 2 |  |  | 25 | GE data. Charging motor engages after a close. |  |  | 1 | Historian CRT | 140 | 140 |  | 1.3725
480V Switchgear Main Breaker 2 | 2 |  |  | 25 | Motor inrush = 25 A, motor windup = 7 A, Trip Coil = 2 A |  |  | 1 | Historian | 985 | 985 |  | 9.6569
Electrically Operated Generator Circuit Breakers | [7 empty] | 1 | ST Work Station CRT | 140 | 140 |  | 1.3725
CTG 9 Breaker CB-CTG9-1 Close |  |  |  | 2.3 |  |  |  | 1 | ST Operator Work Station | 157 | 157 |  | 1.5392
CTG 9 Breaker CB-CTG9-1 Trip | 12.6 | [6 empty] | 2 | CT Work Station CRT | 140 | 280 |  | 1.3725
CTG 9 Breaker CB-CTG9-1 Hyd Pmp Mtr |  |  |  |  | assuming motor engages after a close command - Valley shows AC motor |  |  | 2 | CT Operator Work Station | 157 | 314 |  | 1.5392
CTG 10 Breaker CB-CTG10-1 Close | 12.6 |  |  | 2.3 |  |  |  | 1 | CEMS Data Acquisition CRT | 140 | 140 |  | 1.3725
CTG 10 Breaker CB-CTG10-1 Trip | [7 empty] | 1 | CEMS Data Acquisition WS | 293 | 293 |  | 2.8725
CTG 10 Breaker CB-CTG10-1 Hyd Pmp Mtr |  |  |  |  | assuming motor engages after a close command - Valley shows AC motor |  |  | 1 | 8 Control Room Printers (2 operating at full load, the rest at 10% load) | 830 | 830 |  | 8.1373
STG 8 Breaker CB-STG8-1 Close |  |  |  | 2.3 |  |  |  | 1 | Fire Alarm Panel | 360 | 360 |  | 3.5294
STG 8 Breaker CB-STG8-1 Trip | 12.6 | [6 empty] | 4 | Ethernet Switches | 120 | 480 |  | 1.1765
STG 8 Breaker CB-STG8-1 Hyd Pmp Mtr |  |  |  |  | assuming motor engages after a close command - Valley shows AC motor |  |  | 1 | Emergency Stop Drum Level | 200 | 200 |  | 1.9608
Non-Breaker Loads
Fire Panels (4 @250 VA ea) | 8 | 8 | 8 | 8 |  |  |  |  | CONTROL ROOM TOTALS |  | 6364 | watts
Breaker Test Cabinet
GSU-CTG9-1 Bucholz (63X) | 3 | 3 | 3 | 3 |  |  | HRSG 1 (CEMS)
GSU-CTG10-1 Bucholz (63X) | 3 | 3 | 3 | 3 |  |  |  | Quantity | Item | Watts/Unit | Total Watts
GSU-STG8-1 Bucholz (63X) | 3 | 3 | 3 | 3 |  |  |  | 1 | HRSG CEMS HSL | 5000 | 5000 |  | 49.0196
AUX-CTG9-1 | 3 | 3 | 3 | 3 |  |  |  | 3 | Drum Level Control Units | 216 | 648 |  | 2.1176
AUX-CTG10-1 | 3 | 3 | 3 | 3 |  |  |  | 1 | HRSG Burner Management System | 745 | 745 |  | 7.3039
STG EB/SO PUMP (2hr Min) | 825 | 275 | 0 | 0 | Valley GE data. 40 HP motor 825 Amax LRC, 275 FLA
STG Generator Protection Panel | 20 | 2 | 2 | 2 | Actual transient =~18 A, actual steady state (LOR's not active) ~= .6 A |  |  |  | HRSG 1 (CEMS) TOTALS |  | 6393 | watts
STG 8 Generator Excitation Panel | 3 | 3 | 3 | 3 | All digital loads
STG 8 Generator Synchronizing Panel | 3 | 3 | 3 | 3 | All digital loads |  | HRSG 2 (CEMS)
STG 8 Trip Solenoid for ETD-1 | 1 | 1 | 1 | 1 | Valley leftover data for safety |  |  | Quantity | Item | Watts/Unit | Total Watts
STG 8 Trip Solenoid for ETD-2 | 1 | 1 | 1 | 1 | Valley leftover data for safety |  |  | 1 | HRSG CEMS HSL | 5000 | 5000 |  | 49.0196
STG 8 Trip Solenoid for ETD-3 | 1 | 1 | 1 | 1 | Valley leftover data for safety |  |  | 3 | Drum Level Control Units | 216 | 648 |  | 2.1176
DCS Cabinets | 39 | 39 | 39 | 39 |  |  |  | 1 | HRSG Burner Management System | 745 | 745 |  | 7.3039
DC feed to LADWP substation relay building | 100 | 10 | 10 | 100
?? KVA Inverter | 351.8519 | 351.8519 | 351.8519 | 351.8519 | assuming 95% loaded, 90% efficiency |  |  |  | HRSG 2 (CEMS) TOTALS |  | 6393 | watts
TOTAL | 1465.5419 | 709.8519 | 434.8519 | 673.7519
minutes of duty cycle | 1 | 119 | 119 | 1 |  |  | STG Building
amp*hours | 24.4257 | 1407.8728 | 862.4562 | 11.2292 |  |  |  | Quantity | Item | Watts/Unit | Total Watts
[8 empty] | 1 | Mark VI | 2000 | 2000 |  | 19.6078
[8 empty] | 4 | Ethernet Switches | 120 | 480 |  | 1.1765
L = continuous FLA of UPS
|  | C = Ampere hours emergency discharge | [6 empty] | STG TOTALS |  | 2480 | watts
H = number of hours recharge time required per contract
|  | C = | 2305.9839 |  |  |  | MV SWGR BLDG DCS
|  | L = | 351.8519 |  |  |  |  | Quantity | Item | Watts/Unit | Total Watts
|  | H = | 24 |  |  |  |  | 2 | CT Local HMI | 840 | 1680 |  | 8.2353
Ampere Charger = | 457.5428 | amp minimum | [5 empty] | 10 | LEC Transceivers W/Ethernet | 120 | 1200 |  | 1.1765
[8 empty] | 2 | Hydrogen Control Panel | 200 | 400 |  | 1.9608
UPS VA | 40000
UPS Efficiency % = | 90% | [7 empty] | 4160V SWGR BLDG DCS TOTALS |  | 3280 | watts
STEAM TURBINE LOADS
[8 empty] | Quantity | Item | Watts/Unit | Total Watts
[8 empty] | 1 | Solenoid Power | 2400 | 2400 |  | 23.5294
[9 empty] | STEAM TURBINE LOAD TOTALS |  | 2400 | watts
[7 empty] | SUM PLANT UPS TOTAL WATTS |  |  |  | 27310 | watts
[7 empty] | 25 % MARGIN |  |  |  | 6827 | watts
[6 empty] | TOTAL PLANT UPS WATTS |  |  |  |  | 34137.5 | watts
Note on F33: RJBERLAND: Device numbers, counts and power requirements are hand tallied in the project design notebook.

## DPPP (hidden)
DC LOADS on 125 VDC System
|  | 1st Minute Transients + Continuous | Minutes 1 to 60 | Minutes 61 to 239 | Minute 240 | Normal
BOP Relay Panel |  | 10 | 10 | 10 | 10 | 10
Electrically Operated Breakers
4160V Main Breaker |  | 10.5 | 1 | 1 | 23 | 1 | Haynes values used for trip coils & charging motors
4160V LCI Breaker |  | 10.5 | 1 | 1 | 23 | 1 | Trip coil = 10.5 A, Charging Motor inrush = 23 A
480V Switchgear 1 Main Breaker |  | 2 | 1 | 1 | 25 | 1 | Motor windup = 8 A
480V Switchgear 2 Main Breaker |  | 2 | 1 | 1 | 25 | 1
Emergency Diesel Generator
480V breaker & control panel |  | 1 | 5 | 5 | 5 | 1
Switchyard Circuit Breakers
CB-EL-1 |  | 13.2 | 1 | 1 | 19.8 | 1 | Values from Mitsubishi typical data for type BM1 spring breakers
CB-EL-2 |  | 13.2 | 1 | 1 | 19.8 | 1
CB-EL-3 |  | 13.2 | 1 | 1 | 19.8 | 1
CB-EL-4 |  | 13.2 | 1 | 1 | 19.8 | 1
CB-EL-5 |  | 13.2 | 1 | 1 | 19.8 | 1
Transformers
GSU-CTG-01 |  | 2 | 2 | 2 | 2 | 2
GSU-STG-01 |  | 2 | 2 | 2 | 2 | 2
UAT-AUX-1 |  | 2 | 2 | 2 | 2 | 2
SUS-XFMR-1 |  | 2 | 2 | 2 | 2 | 2
SUS-XFMR-2 |  | 2 | 2 | 2 | 2 | 2
DCS Cabinets
Control Room Equipment |  | 10 | 10 | 10 | 10 | 10
DCS Room Cabinets |  | 10 | 10 | 10 | 10 | 10
Swgr Bldg Cabinets |  | 10 | 10 | 10 | 10 | 10
HRSG Cabinets |  | 10 | 10 | 10 | 10 | 10
WT Cabinets |  | 10 | 10 | 10 | 10 | 10
Steam Turbine Loads | [6 empty] | See Fuji "Power Supply Assignment Requirement" (202-ES-0016-01)
Turbine Generator Regulation Panel (S-TGR) |  | 10 | 10 | 10 | 10 | 10 | 1.0 kW
Thyristor (THY) |  | 0 | 0 | 0 | 0 | 0 | 10 kW only for initial field energization
|  | 15 | 15 | 15 | 15 | 15 | 1.5 kW
Turbine Protection Panel (S-TPR) |  | 30 | 30 | 30 | 30 | 30 | 3.0 kW
Generator Protection Panel (S-GPR) |  | 15 | 15 | 15 | 15 | 15 | 1.5 kW
STG DCS cabinets (S-DCS) |  | 35 | 35 | 35 | 35 | 35 | 3.5 kW
125VDC Motor Control Center (S-DMS) |  | 204 | 80 | 0 | 0 | 0 | 204A for acceleration, and sustained operation at 1.15 SF
|  | 2 | 2 | 2 | 2 | 2 | 200 W for control
*emergency jacking oil pump* |  | 0 | 0 | 0 | 0 | 0 | worst case if there is emergency requirments for jacking oil
Miscellaneous
Duct Burner PLC |  | 2 | 2 | 2 | 2 | 2
Air Compressor PLC |  | 2 | 2 | 2 | 2 | 2
CEMS PLC |  | 2 | 2 | 2 | 2 | 2 |  | Battery Notes:
Fire Alarm System |  | 2 | 2 | 2 | 2 | 2 |  | 1. Batteries will supply power for a 4 hour period maximum.
2. ELOP will start (Inrush duration < 1 min) at beginning of 4 hr period and run for 1 hour max.
3. Trip loads will occur for less than 1 minute at beginning of 4 hr period.
30kVA Inverter |  | 150 | 150 | 150 | 150 | 150 | assumed 50% load | 4. Close loads will occur for less than 1 minute at end of 4 hr period.
| TOTAL | 631 | 429 | 349 | 535 | 345 |  | 5. 60 cell battery with Float voltage - 2.25 vpc and Final voltage 1.75 vpc
Design Margin (%) | 4 | 656.24 | 446.16 | 362.96 | 556.4 | 358.8 |  | 6. Lead-acid calcium plate battery.
| minutes of duty cycle | 1 | 59 | 179 | 1
| amp*hours | 10.9373 | 438.724 | 1082.8307 | 9.2733 |  | Constant amperage draw under normal operation | Battery Charger Notes:
1. Two 100% capacity battery chagers are required.
2. Chargers to supply 100% DC continuous loads as well as item 3 below.
[5 empty] | L = plant load at normal conditions |  |  | 3. Recharge batteries from fully discharged state within 12 hour period.
[5 empty] | C = Ampere hours emergency discharge |  |  | 4. Charger input to be 600VAC, 3-phase.
H = number of hours recharge time required per contract
|  |  | C = | 1541.7653
|  |  | L = | 358.8
|  |  | H = | 12
| Ampere Charger = | 500.1285 | amp minimum
LMG Add Ons
| DCS Total | 50 | A
| UPS Total | 150 | A
| Normal Total | 358.8 | A
| Charger Efficiency | 90%
| 480V Charger Feed | 83.5501 | A
| Total Charger Aux Power (Normal) | 44.85 | kW
| Breakout - UPS Aux Power | 18.75 | kW
| Breakout - DCS Aux Power | 6.25 | kW
| Breakout - Charger Aux Power (Normal) | 19.85 | kW
Note on H46: RJBERLAND: Device numbers, counts and power requirements are hand tallied in the project design notebook.

## Temperature Correction
IEEE Std 485-1997
IEEE Recommended Practice for Sizing Lead-Acid Batteries for Stationary Applications
From IEEE 485-1997 | 6.2.2
The available capacity of a cell is affected by its operating temperature. The standard temperature for rating
cell capacity is 25 C (77 F). If the lowest expected electrolyte temperature is below this standard tempera-
ture, select a cell large enough to have the required capacity available at the lowest expected temperature. If
the lowest expected electrolyte temperature is above 25 C (77 F), it is a conservative practice to select a
cell size to match the required capacity at the standard temperature and to recognize the resulting increase in
temperatures for vented lead-acid cells with nominal 1.215 specifc gravity. For unlisted temperatures within
the range of Table 1, interpolate between adjacent values and round off to two decimal places. For VRLA
cells, check with the manufactureers for the apporpriate temperature correction factors.
Table 1. Cell size correction factors for temperature
Electrolyte temp (F) | Cell size correction factor
25 | 1.52
30 | 1.43
35 | 1.35
40 | 1.3
45 | 1.25
50 | 1.19
55 | 1.15
60 | 1.11
65 | 1.08
66 | 1.072
67 | 1.064
68 | 1.056
69 | 1.048
70 | 1.04
71 | 1.035
72 | 1.029
73 | 1.023
74 | 1.017
75 | 1.011
76 | 1.006
77 | 1
78 | 0.994
79 | 0.987
80 | 0.98
81 | 0.976
82 | 0.972
83 | 0.968
84 | 0.964
85 | 0.96
86 | 0.956
87 | 0.952
88 | 0.948
89 | 0.944
90 | 0.94
95 | 0.93
100 | 0.91
105 | 0.89
110 | 0.88
115 | 0.87
120 | 0.86
125 | 0.85

## Notes
BATTERY AND CHARGER SIZING WORKSHEET NOTES
General
Green cells are automatically calculated. Yellow cells are to be altered by the user based on project requirements.
Blue cells contain typical data. These cells should be checked by the user and altered if needed.
Battery Size Calculation
Sizing equation for determining the capacity of the battery bank.
H= | time (hours) operating in in current segment of duty cycle
A= | amount of current (amps) required to operate in current segment of duty cycle
Cb= | battery capacity needed under ideal circumstances
DM= | design margin in % to account for unknown/miscellaneous loads
T= | assume 1.000 for calculations @ 77 F.
If another temp is desired, see Temperature Correction Tab
A= | Age factor, to account for battery quality loss as they age
Charger Size Calculation
Sizing equation for determining the size of the battery charger from IEEE Std 946-2004:
Equation 1: | I1 = L + (1.1 x C) / H
Equation 2: | I2 = ILC + L
I1 = | Is the minimum required charger rated output (in amperes). Battery manufacturers often recommned that the charging rate be limited; typical values are 10% to 20% of the 8 h capacity. I1 should be evaluated for the maximum and minumum values of L.
I2 = | is the minimum charger output (in amperes) that will supply the maximum operating load.
I3 = | is the recommended charger rated output (in amperes); i.e., the larger of I1 and I2. If it can be demonstrated that the reduction in battery capacity that results during and following the application of Ln does not compromise the ability fo the battery to satisfy its intended function, the user may select Equation (1) as the basis of sizing the battery charger(s). Battery manufacturers often recommend that the charging rate be limited; typical values are 10% and 20% of the 8 h capacity. I3 should be evaluated for the maximum values of ILC.
ILC = | is the continuous dc load (in amperes), including future load growth.
L = | is the largest combination of non-continuous loads (as defined in 4.2.2 of IEEE Std 485-1997) that would likely be connected to the bus simultaneously during normal plant operation, including periodic testing of dc components such as emergency lighting and emergency oil pumps.
1.1 = | is the constant that compensates for battery losses.
C = | is the discharge from the battery measured in ampere-hours. After discharge testing as defined in IEEE Std 450-2000, it is convenient to assume that the ampere-hours removed by the test can be replaced in 8 h to 24 h. For users meeting the requirements of IEEE Std 308-2001, the ampere-hours removed by the duty cycle is appropriate.
H = | is the time to recharge the battery to approximately 95% of capacity (in hours). To minimize dc system downtime, a reasonable recharge time should be selected; 8 h to 24 h is recommended. It is recommended that the battery manufacturer be consulted for values of T less than 8 h.