## Checklist
ETAP
ESTIMATING DEPARTMENT CHECKLIST
Project Number: |  | Revision Type | IFP
Revision Letter or Number:
Project Name: |  | Responsible Engineer's Printed Name:
File Names: |  | Checker's Printed Name:
Lead's Printed Name:
Review Date:
Department Manager's or Lead's Initials:
Checker to Confirm that… ELECTRICAL EQUIPMENT |  |  | Initials
|  |  | Engineer | Checker | Lead
1 | EEGL-880C: Design Guideline for Auxiliary Electrical System Analysis has been reviewed
2 | Bus ratings are consistent with RFP requirements (Voltage, Amp, Short Circuit)
3 | If ratings vary from RFP, it is specified below, and included in the Clarifications Log
4 | Transformer ratings are in compliance with RFP requirements (cooling type, impedance)
5 | If ratings vary from RFP, it is specified below, and included in the Clarifications Log
6 | All unique requirements from the RFP are listed below
7 | Equipment ratings that are used can be provided
8 | Medium voltage switchgear ratings (1200A, 2000A, 3000A) or (avoid 4000A bus as much as possible)
9 | Transformer impedances are consistent with manufacturer standards (IEEE C57.12.10, within 1%)
10 | Transformer standard X/R values are input
11 | Oil Filled transformer sizing is consistent with IEEE C57.12.10
12 | Transformer tap settings have been selected and are consistent for all studies.
13 | Transformer impedance tolerances are set to +/- 7.5% for two winding and +/-10% for three winding transformers.
14 | Site temperature and altitude has been input for transformer modeling
15 | Grounding Systems have been identified and meet RFP Requirements
16 | Medium Voltage System: Low Resistance Ground
17 | Low Voltage System: High Resistance Ground
18 | Cable sizing and lengths have been input for MV system and low voltage switchgear and feeders
19 | Equipment identified and tags have been cross checked One-Line and Load lists.
20 | Redundancy requirements have been met
21 | Redundant UAT and SUS where applicable
22 | Double ended busses where applicable
23 | Alternate power supply where applicable
24 | Redundant Loads are modeled according to load list
25 | Power Transformations are minimized (If 13.8kV Bus is required, All SUS transformers are fed from this bus)
26 | Stand-by / Emergency Generation has been included if required
27 | Generator requirements and ratings are correct.
28 | Modeled as Voltage Controlled
29 | Modeled correctly for each load flow study (off-line, full load, max/min voltage)
30 | Voltage minimum is set to .95 per unit and maximum to 1.05 per unit.
31 | Utility Source requirements and ratings are consistent with RFP requirements
If the Utility Source criteria is not provided: Voltage Min = 95%, Voltage Max =105%, Short Circuit = 45kA
32 | No motors below 3000HP are fed from the 13.8kV Bus (IEEE 666-2007)
33 | All Loads 1500HP and above are fed from a breaker (KPE Standards)
34 | Fire Pumps are fed from the MV switchgear (KPE Standards)
35 | Motor loads and lumped loads have been cross checked with the load list
36 | GSU Calculation has been completed and values have been cross checked
37 | All case studies are described below, and have been included in the design basis spreadsheet
38 | Load Flow Study has been completed for Normal, Worst, and Light Load Cases
39 | Steady state voltages are within KPE (> 90%) and RFP requirements when grid voltage are minimized
40 | Steady state voltages are within KPE (< 110%) and RFP requirements when grid voltage are maximized
41 | Motor Starting Study has been completed for Worst Cases
42 | Voltage dips remain within KPE (above 80%) and Client standard requirements
43 | When starting multiple motors at the same time, line voltage remains above 85% (required for contactors to close)
44 | When starting VFD's, the line voltage remains above 90%
45 | Starting of the largest motor at each voltage level has been analyzed
46 | Larges motors on same voltage level that are fed from different sized transformers have both been analyzed
47 | Starting motors with very long feeders has been analyzed
48 | If the largest motor on any voltage level is a VFD, than the largest direct-on-line motor has also been analyzed
49 | Short Circuit Study has been completed for Worst Cases
50 | Short circuit current remains under equipment ratings plus the RFP design margin (10% if not specified)
51 | Worst case scenario was analyzed with all tie breakers closed, generators and all normal load on-line.
52 | Pre-fault voltage is set to 105%
53 | The adjusted X/R short circuit value remains under the equipment rating and design margin.
Notes and Clarifications |  |  | Reference Documents
EEGL: 800C
Load List
Clarifications Log
IEEE 666-2006
IEEE C57.12.10
One-Line
GSU Calculation

## Load Flow
Engineer to update tag numbers and ratings per project requirments and input results from ETAP load flow studies. All results will need to be verify again with updated project information before engineered equipment QCS review. | [8 empty] | Information listed below is an example. Engineer to update the information below for each project. Configuration setup to be reviewed with the lead prior to running the studies.
Load Flow Results | [8 empty] | Normal Configuration - Load Flow
Bus Tag Number | Nominal Bus Voltage | Bus Current Rating | Base Configuration |  | Worst Case Configuration |  | Lightly Loaded Configuration |  | 1 | Minimum switchyard contribution connected and voltage set to nominal rating (100%)
|  |  | Voltage (% of Nominal) | Current (A) | Voltage (% of Nominal) | Current (A) | Voltage (% of Nominal) | Current (A) | 2 | Medium and low voltage switchgear tie breakers are open, all UAT's and SST's are in operation
5kV-SWGR-01A | 4.16kV | 3000A | [6 empty] | 3 | All generators are on line, excitation loads energized and LCI/SFC loads are not energized
5kV-SWGR-01B | 4.16kV | 3000A | [6 empty] | 4 | Standby/Emergency generators are not in service
BOP-SWGR-01A | 480V | 4000A | [6 empty] | 5 | Secondary/emergency feeds from utility or other sources are not in service
BOP-SWGR-01B | 480V | 4000A | [6 empty] | 6 | Normally operating 5kV lods are in service and redundant loads are not in service
BOP-SWGR-02A | 480V | 4000A | [6 empty] | 7 | 480V lumped loads and static loads are in service, loading to be in line with project load list.
BOP-SWGR-02B | 480V | 4000A | [7 empty] | - lumped load constant kVA/constant Z percentage updated to match MCC loading
[9 empty] | 8 | Tap setting of UAT's set at -2.5% on the high side, SST transformers are at their nominal tap setting.
Worst Case Configuration - Load Flow
[9 empty] | 1 | Minimum switchyard contribution connected and voltage set to 95% of nominal rating
[9 empty] | 2 | Medium voltage tie breaker is closed (one UAT out of service)
[9 empty] | 3 | Unit 1 CTG starting - LCI/SFC load energized and excitation load for Unit 1 at 10% of nominal load. Remaining units on line and excitation loads energized at nominal rating.
[9 empty] | 4 | Standby/Emergency generators are not in service
[9 empty] | 5 | Secondary/emergency feeds from utility or other sources are not in service
[9 empty] | 6 | Normally operating 5kV lods are in service and redundant loads are not in service. (Confirm with mechnical worse case sceneraio for number of medium voltage motors running, e.g. bypass case where all BFP need to be in operation)
[9 empty] | 7 | 480V lumped loads and static loads are in service, loading to be in line with project load list.
- lumped load constant kVA/constant Z percentage updated to match MCC loading
[9 empty] | 8 | Tap setting of UAT's set at -2.5% on the high side, SST transformers are at their nominal tap setting.
Lightly Loaded Configuration - Load Flow
[9 empty] | 1 | Minimum switchyard contribution connected and voltage set to 105% of nominal rating
[9 empty] | 2 | Medium and low voltage switchgear tie breakers are open, all UAT's and SST's are in operation
[9 empty] | 3 | All generators are off-line, all LCI/SFC and excitation loads are not energized
[9 empty] | 4 | Standby/Emergency generators are not in service
[9 empty] | 5 | Secondary/emergency feeds from utility or other sources are not in service
[9 empty] | 6 | No 5kV motors are in service
[9 empty] | 7 | Non-essentail 480V loads are not in service
- Lumped MCC loads should have the loading percentage adjusted to only account for essential loads being energized
[9 empty] | 8 | Tap setting of UAT's set at -2.5% on the high side, SST transformers are at their nominal tap setting.

## Short Circuit
Engineer to update tag numbers and ratings per project requirments and input results from ETAP load flow studies. All results will need to be verify again with updated project information before engineered equipment QCS review. | [9 empty] | Information listed below is an example. Engineer to update the information below for each project. Configuration setup to be reviewed with the lead prior to running the studies.
Short Circuit Results | [9 empty] | Worst Case Configuration - Short Circuit
Bus Tag Number | Equipment Interrupting Rating (kA) | Equipment Momentary Rating (kA)* | Equipment Peak Rating (kA)** | Worst Case Configuration | [5 empty] | 1 | Maximum SWYD contribution connected
|  |  |  | Interrupting (kA) | Interrupting Margin (%) (Calculated) | Momentary (kA) | Momentary Margin (%) (Calculated) | Peak(kA) | Peak Margin (%) (Calculated) | 2 | Pre-fault voltages set to 105% on nominal
5kV-SWGR-01A | 50 | 78 | 130 |  | 100% |  | 100% |  | 100% | 3 | All busses are faulted
5kV-SWGR-01B | 50 | 78 | 130 |  | 100% |  | 100% |  | 100% | 4 | Medium voltage and low voltage tie breakers are closed, no busses are being paralled (one only main breaker closed)
BOP-SWGR-01A | 85 | 113 | N/A |  | 100% |  | 100% | N/A | #VALUE! | 5 | All generators are on line
BOP-SWGR-01B | 85 | 113 | N/A |  | 100% |  | 100% | N/A | #VALUE! | 6 | Normally operating 5kV motors are connected and redundant motors are disconnected except for both primary and backup BFP on each HRSG are in operation due to bypass case condition
BOP-SWGR-02A | 65 | 86 | N/A |  | 100% |  | 100% | N/A | #VALUE! |  | - confirm with mechnical for cases where any primary and redundant motors will be in operation, confirm worst case operation (e.g. does fuel oil firing condition lead to higher kA ratings or does gas firing due to fuel gas compressors being in operation)
BOP-SWGR-02B | 65 | 86 | N/A |  | 100% |  | 100% | N/A | #VALUE!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
[5 empty] | #DIV/0! |  | #DIV/0! |  | #DIV/0!
*Momentary rating for medium voltage equipment is 1.55 times the interrupting rating, low voltage equipment is 1.33 for unfused breakers and 1.247 for fused circuit breakers
**Peak rating for medium voltage equipment is 2.6 times the interrupting rating, rating not valid for low voltage equipment

## Motor Starting
Engineer to update tag numbers and ratings per project requirments and input results from ETAP load flow studies. All results will need to be verify again with updated project information before engineered equipment QCS review. | [7 empty] | Information listed below is an example. Engineer to update the information below for each project. Configuration setup to be reviewed with the lead prior to running the studies.
Load Flow Results | [7 empty] | Normal Configuration - Motor Starting
Bus Tag Number | Nominal Bus Voltage | Base Configuration |  |  | Worst Case Configuration |  |  | 1 | Minimum switchyard contribution connected and voltage set to nominal rating (100%)
|  | Pre-Start Voltage (% of Nominal) | Start Voltage (% of Nominal) | Post Start Voltage (% of Nominal) | Pre-Start Voltage (% of Nominal) | Start Voltage (% of Nominal) | Post Start Voltage (% of Nominal) | 2 | Medium and low voltage switchgear tie breakers are open, all UAT's and SST's are in operation
5kV-SWGR-01A | 4.16kV | [6 empty] | 3 | All generators are on line, excitation loads energized and LCI/SFC loads are not energized
5kV-SWGR-01B | 4.16kV | [6 empty] | 4 | Standby/Emergency generators are not in service
BOP-SWGR-01A | 480V | [6 empty] | 5 | Secondary/emergency feeds from utility or other sources are not in service
BOP-SWGR-01B | 480V | [6 empty] | 6 | Normally operating 5kV lods are in service and redundant loads are not in service
BOP-SWGR-02A | 480V | [6 empty] | 7 | Starting third fuel gas compressor motor
BOP-SWGR-02B | 480V | [7 empty] | - select largest 5kV motor for motor starting study, confirm with mechincal worst case condition (e.g. starting back up fuel gas compressor or BFP with normally operating pumps connected)
[8 empty] | 8 | 480V lumped loads and static loads are in service, loading to be in line with project load list.
- lumped load constant kVA/constant Z percentage updated to match MCC loading
[8 empty] | 9 | Tap setting of UAT's set at -2.5% on the high side, SST transformers are at their nominal tap setting.
Worst Case Configuration - Motor Starting
[8 empty] | 1 | Minimum switchyard contribution connected and voltage set to 95% nominal rating
[8 empty] | 2 | Medium voltage switchgear tie breaker is closed and one main breaker is open (one UAT out of service)
[8 empty] | 3 | All generators are on line, excitation loads energized and LCI/SFC loads are not energized
[8 empty] | 4 | Standby/Emergency generators are not in service
[8 empty] | 5 | Secondary/emergency feeds from utility or other sources are not in service
[8 empty] | 6 | Normally operating 5kV lods are in service and redundant loads are not in service
[8 empty] | 7 | Starting third fuel gas compressor motor
- select largest 5kV motor for motor starting study, confirm with mechincal worst case condition (e.g. starting back up fuel gas compressor or BFP with normally operating pumps connected)
[8 empty] | 8 | 480V lumped loads and static loads are in service, loading to be in line with project load list.
- lumped load constant kVA/constant Z percentage updated to match MCC loading
[8 empty] | 9 | Tap setting of UAT's set at -2.5% on the high side, SST transformers are at their nominal tap setting.