## Notes
ELECTRICAL Design Philosophy Checklist
ITEM | NOTES
1 | Note this sheet is not to supersede the RFP. This is information used by the KPC Estimators to align themselves with the standards and philosophy of our Engineering Partner.
2
3
4
5
6
7
8
9
10

## Inst. Design Philosophy
Instructions: Form is already filled out for KPE standards. Confirm with RFP. If KPE is not the Engineer on the estimate, clear the sheet and send to Engineer.
Project Name:
Initials From Engineer | Standards and Philosophy for Instrumentation Estimate | KED Standard |  |  |  | Comments - Notes
Tubing Standard - Philosophy
| What wall thickness will be used for steam tubing? | 0.065 | 0.049 | 0.083 | Other | Confirm with there are no unusually high pressures with mechanical. If so, use .083 for HP steam and BFW.
| What systems will 0.083 wall thickness tubing? | HPS
| Minimum tubing diameter | 1/2" | 1/4" | 3/8" |  | KED Standard, I-2 Instrumentation Spec
| What wall thickness will be used for all other process tubing? | 0.049 | 0.065 |  | Other
| What wall thickness will be used for instrument air tubing? | 0.049 | 0.065 |  | Other
| What type of tubing shall be used for instrument air at the air user connection? | Flex Hose | Stainless Steel |  | Other | KP best practice is to use stainless braided flex hose.
| Will aluminum or galvanized steel be used for tube tray? | Aluminum | Galvanized Steel |  | Other
| Tray for impulse (bare) lines | Galvanized Steel | Aluminum
| If the RFP does not specify minimum wall tubing, is it required by the Engineer's internal standards? | No | Yes | No
| Will Engineering be procuring the CEMS tubing? Instrumentation picks up the labor, Mechanical picks up the tube bundle purchase | Yes | No | No
| Will the Turbine vendor(s) supply any loose shipped tubing? Please provide quantity in linear feet. (Combustion Turbine Only) See inst. PM sheet for typical quantities | Yes | No | No |  | Depends on Turbine Manufacturer
| How many volume bottles (a.k.a. volume booster tank), if any, are expected for this project? (Usually found on large, severe service valves in critical systems) | Other | 10 | 20 | 30 | Confirm with mechanical that only bypass valves require volume bottles. Typical for a 2X1 is 10
| Additional Items (From the Engineer to the Estimator) | Please Make Comments Here
Pressure/Temperature Standard - Philosophy
| Will any pressure gauges on the boilers require freeze protection? (Combined Cycle only) | Other | Yes | No |  | KP procured gauges will have diaphragm seals and not require additional freeze protection.
| At what frequency should expansion loops be installed on sample lines? | Other | 1 at instrument |  |  | Consult with mechanical on project specific basis.
| If steam drums on top of the HRSG are not enclosed, do instruments and impulse lines need to be heat traced? | Other | Yes | No |  | Typically Yes, but project location may dictate
| Additional Items (From the Engineer to the Estimator) | Please Make Comments Here
Calibration Standard - Philosophy
| Will the instruments procured with the engineered equipment be supplied with calibration certificates? | Yes | No
| If yes, will the instruments need to be (re-)calibrated on-site? | No | Yes |  |  | Verify with RFP and enter clarification into the C/E Log.
| Will the vendor supplied instruments be supplied with calibration certificates? | No | Yes
| If yes, will the instruments need to be (re-)calibrated on-site? | No | Yes
| Additional Items (From the Engineer to the Estimator) | Please Make Comments Here
Standard - Philosophy
| Will the Iso-Phase require pressurized air? | Yes | No
| If yes, will the pressurized air be combined for the phases or separate control systems for each phase? | Combined | Separate | Separate
| For transmitters located outside, which type(s) will need heated enclosures and what systems are they on? | Pressure, Flow & Level Transmitters | None | Other |  | All water and steam
| For lines not heat traced - Which systems or lines need personnel protection and what is the distance requirement? | Other | 7ft | 3ft |  | Confirm with mechanical that only bypass valves require volume tanks.
| Will seal pots be used on steam and/or gas systems for this project? | Steam only | Gas only | Both | No | KP standard is steam and BFW flow elements only.
| Are blowdown valves required? | Yes | No |  |  | Follow up on specific systems that may require 2 per
| Are transmitters procured as engineered equipment furnished with manifold installed? | Yes | No
| Instrument stand design, Is this project using the KED Standard instrument stand? | Yes | No |  |  | See Here for Std. Detail Drawings
| Additional Items (From the Engineer to the Estimator) | Please Make Comments Here
| Answered by: | Date:
Estimate Lead Signature: