## Instructions
Task Number
1 | Confirm DCS Cabinet locations and descriptions.
If DCS Cabinet Locations Names change:
| A. | Modify names on "IO Count" table of the "Overview" tab only
| B. | Modify names in "DCS CAB" column of the "DCS IO Count" tab only
If DCS Cabinet Locations are added/deleted:
| A. | Add/delete rows with desired locations on the "IO Count", "IO Cards", and "Remote IO Cabinets" tables on the "Overview" tab
| B. | Modify names on "IO Count" table of the "Overview" tab only
| C. | Modify names in "DCS CAB" column of the "DCS IO Count" tab only
Confirm Spare Requirements from RFP
| A. | IO Spare refers to spare terminations on installed IO cards
| B. | Cabinet spare refers to spare space to install future IO cards
| C. | IO Margin field is for internal use only to add margin depending on confidence of IO count
2 | P&ID Count
| A. | Add/delete rows for P&IDs as needed
| B. | Put the total number of each device type on each P&ID in the "Quantity" column on the "DCS IO Count" tab (See the "Signal Philosophy Tab" for device type descriptions)
| C. | Do not count the motors off the P&IDs, use the load list
| D. | Put the total number of instruments in the IO type columns (See the "Signal Philosophy Tab" for instrument IO types)
3 | One-Line Count
| A. | Put the total number of devices (mains, ties, feeder breakers) in the IO type columns (See the "Signal Philosophy Tab" for instrument IO types)
4 | Load List
| A. | Put the total number of motors (MCCs) in the IO type columns (See the "Signal Philosophy Tab" for instrument IO types)
5 | Vendor Information
If given a vendor I/O List:
| A. | Put the total number IO in the appropriate IO type columns (See the "Signal Philosophy Tab" for device type descriptions if needed)
If given vendor P&IDs: follow P&ID count instructions
Check RFP for unique hardwired interfaces (water treatment, duct burner, aux boiler)
6 | Options
Review the RFP to to determine the following:
| A. | Number of workstation components and furniture. See sections 1 and 7.
| B. | Datalink Connections to PLCs. If the RFP is silent on this subject, Kiewit standard is to have redundant datalinks to turbine control systems, switchyard and smart switchgear/MCCs. All other datalinks should be non-redundant. See section 2.
| C. | What is controlled by the DCS and what is controlled by PLCs. If the RFP is silent on this subject, the Kiewit standard is to control pre packaged systems such as water treatment, aux boiler, FG/air compressors, duct burner, etc. by PLCs. See section 3.
| D. | What graphics from other control systems need to be duplicated on the DCS. If RFP is silent on this subject, the Kiewit standard is to not duplicate turbine/PLC graphics. See section 5.
| E. | Network and time sync preferences. See section 7.

## Overview
Project Name: |  |  | Numbers below do not include the spare margin listed.
Project Number: |  |  | I/O Spare: |  |  | %
Rev: |  |  | Cabinet Spare: |  |  | %
IO Count
|  | DI | DI_SOE | DO | DO_10A | AI | AI_HZT | AO | TE | RTD | Wireless | Datalink | Total
| Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL= | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*Adjust I/O Margin based upon your level of confidence in the documents used to create the I/O count.
I/O Margin:
Use Cabinet Counts for the Enclosure Layouts *Do not send Cabinet Count to Vendors*
*Use Card Counts to determine cabinet counts for enclosure layouts, do not send to vendors*
| IO Cards | [13 empty] | Remote IO Cabinets
|  | DI | DI_SOE | DO | DO_10A | AI | AO | TE | RTD | Wireless | Datalink | Total
| Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Elec Encl | 0
| WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | WTT | 0
| Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Cooling Twr | 0
| STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | STG | 0
| HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | HRSG 1A | 0
| HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | HRSG 1B | 0
| Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Fuel Gas | 0
| Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Raw Wtr | 0
| TOTAL= | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | TOTAL= | 0
*These are Emerson counts, do not send to vendors*
Channels Per Card
|  |  | DI | 16
|  |  | DI_SOE | 16
|  |  | DO | 16 | 1.5 slots per card
|  |  | DO_10A | 12 | 1.5 slots per card
|  |  | AI | 8
|  |  | AI_HZT | N/A
|  |  | AO | 4
|  |  | TE | 8
|  |  | RTD | 8
|  |  | Wireless | 100 | Points per Hub |  |  |  | *Wireless Hubs are mounted externally from the Cabinets*
|  |  | Datalink | 1 | RS-485 or RS-232

## DCS IO Count
Document Type | Document Number | DESCRIPTION | Quantity | DCS CAB | DI | DI_SOE | DO | DO_10A | AI | AI_HZT | AO | TE | RTD | Wireless | Datalink | Comments
P&ID | PS- | Instrumentation |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Open/Close Pneumatic Valve |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load List |  | MCC Motor Starter |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CT |  | Elec Encl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
|  | Vendor IO |  | Elec Encl | [11 empty] | Vendor
P&ID | PS- | Instrumentation |  | WTT
P&ID | PS- | Open/Close Pneumatic Valve |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | WTT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | PLC Interface |  | WTT
|  | Vendor IO |  | WTT | [11 empty] | Vendor
P&ID | PS- | Instrumentation |  | Cooling Twr
P&ID | PS- | Open/Close Pneumatic Valve |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | Cooling Twr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Instrumentation |  | STG
P&ID | PS- | Open/Close Pneumatic Valve |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ST |  | STG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
P&ID | PS- | Instrumentation |  | HRSG 1A
P&ID | PS- | Open/Close Pneumatic Valve |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HRSG |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
|  | SCR |  | HRSG 1A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
P&ID | PS- | Instrumentation |  | HRSG 1B
P&ID | PS- | Open/Close Pneumatic Valve |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | HRSG |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
|  | SCR |  | HRSG 1B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Vendor
P&ID | PS- | Instrumentation |  | Raw Wtr
P&ID | PS- | Open/Close Pneumatic Valve |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | Raw Wtr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Instrumentation |  | Fuel Gas
P&ID | PS- | Open/Close Pneumatic Valve |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Modulating Pneumatic Valve |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Motor Operated Valve |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | Control Panel |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID | PS- | PLC Interface |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P&ID / One-Line |  | MCC Motor Starter |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Motor Feeder Swgr Breaker |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Main/Tie/Xfmr Feeder Swgr Breaker |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
One-Line |  | Switchgear Main/Tie Breaker |  | Fuel Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Options
1 | Workstations and Printers (Check RFP for quantities. If RFP is silent, use the quantities below.)
|  | 1 | Engineering Workstation with dual 24" monitors
|  | 2 | Operator Workstations with dual 24" monitors
|  | 0 | Temporary workstation for use during commissioning
|  | 1 | Anti-Virus Workstation (Confirm with RFP that this is needed for NERC)
|  | 1 | Historian Workstation with dual 24" monitors
|  | 0 | Asset Management Workstation
|  | 2 | Laser Color Printer
2 | Foreign Device Interfaces (Datalinks)
|  | Redund | Points | Eqiupment Type and Protocol
|  | Y | 1000 | CTG 1 - Modbus Ethernet
|  | Y | 1000 | CTG 2 - Modbus Ethernet
|  | Y | 1000 | STG - Modbus Ethernet
|  | Y | 1000 | STG - Modbus Ethernet
|  | Y | 250 | MV Relays, Swgr, MCCs - Modbus Ethernet
|  | Y | 250 | LV Relays, Swgr, MCCs - Modbus Ethernet
|  | Y | 200 | Switchyard RTU - Modbus Ethernet
|  | Y | 200 | Switchyard RTU - Modbus Ethernet
|  | N | 500 | Water Treatment PLC - Allen Bradley Ethernet
|  | N | 200 | Aux Boiler PLC - Allen Bradley Ethernet
|  | N | 50 | Duct Burner 1 PLC - Allen Bradley Ethernet
|  | N | 50 | Duct Burner 2 PLC - Allen Bradley Ethernet
|  | N | 50 | CEMS 1 - Modbus Ethernet
|  | N | 50 | CEMS 2 - Modbus Ethernet
|  | N | 50 | Air Compressor - Modbus Ethernet
|  | N | 20 | Fuel Gas Metering Station - Modbus Ethernet
3 | Atypical Control to be Implemented in DCS
| place "x" next to equipment to be controlled by DCS instead of PLC |  | Equipment Type
Water Treatment
Aux Boiler
Duct Burner BMS
4 | Number of BOP Graphics
|  | xxx | Custom Graphic Displays (50 typical for 1x1, 70 typical for 2x1)
|  | 20 | Trend Displays
|  | 1 LOT | Periodic, Trip, SOE Logs
|  | 160 | Permissive Displays (pop-ups)
5 | Other Control System Graphic Duplications
|  | 10 | Per CTG
|  | 15 | Water Treatment
6 | NERC CIP - Version 5 Compliant (Check RFP for details regarding NERC CIP)
| place "x" next to equipment to be included |  | Security Information and Event Management System (SIEM) capable of third party interface (Medium impact rating only)
Patch Management System capable of third party interface (Medium impact rating only)
Firewall via DMZ router (Low or Medium impact)
Keypad or Badge Reader Entry for Cabinets for cabinets outside of PSP (Medium impact only)
7 | Additional Hardware
|  | 1 LOT | Operator Console/Control Room Furniture
|  |  | xxx | Emergency Stop Pushbutton Panel with x buttons. (include 1 button for each turbine, duct burner and 1 for plant gas supply)
|  |  | xxx | Drum Level Indicator Panel (1 for each HRSG)
Network Time Server/Satellite Clock-Symmetricom XLi 1U or equal with minimum of 4 IRIG-B AM outputs
IRIG-B Distribution Amplifier (Used if additional clock sync connections are needed)
Configurable Ethernet Switch (Used if additional clock sync connections are needed)
|  | 1 LOT | Network Equipment - All routers, switches, media converters, etc. required for DCS use
Shipped loose - Fiber to Ethernet Copper Media Converters (Etherwan EL-900 or Equal) (review IC dwg to determine qty based on datalinks)
Shipped loose - Fiber to Serial Copper Media Converters (MED-100A or Equal) (review IC dwg to determine qty based on datalinks)
|  | 1 | Spare Network cabinet with dual power feed terminals, transfer switch(es), five shelves for misc. equipment, and a rack mounted patch panel capable of accepting 32 ST fiber connections, and a 16 bay media converter rack (Etherwan EMC1600 or similar) with Fiber to Ethernet media converters (Etherwan EL-110 or Similar).
Marshalling Cabinets and disconnect terminal blocks (only if required by RFP)
8 | Factory Acceptance Test - Buyer/Owner Witness
Weeks for Power Block (3 typical for 2x1, 2 typical for 1x1 or scrubber)
|  | 1 | Week for Datalink Communication Test including simulation of each datalink
|  | 1 | Additional week for atypical DCS control (review section 3)
9 | Additional Options
|  | 3 | Engineering Software Licenses (One permanent, two additional for use during commissioning)
Review RFP requirements for interface with Owner systems to see if an Enterprise Data Server (Ovation specific equipment) option is required
Detailed Operation and Maintenance (O&M) documentation (confirm with RFP the quantity of hard copies required)
10 | Shipments
| Confirm Cabinet Locations and Descriptions |  | Electrical Enclosure Vendor (Location TBD)
Elec Encl RIO Cabinet
Cooling Twr RIO Cabinet
STG RIO Cabinet
HRSG 1A RIO Cabinet
HRSG 1B RIO Cabinet
Fuel Gas RIO Cabinet
Raw Wtr RIO Cabinet
Site - (Insert Site location)
Operator and Engineering Workstations
Controller Cabinets
Network Cabinets
Other RIO Cabinet (if not in electrical enclosure)

## Signal Count
Values in table denote what the Quantity in the DCS IO Count is multiplied by.
See Signal Philosophy Tab for explanation
DESCRIPTION | DI | DI_SOE | DO | DO_10A | AI | AI_HZT | AO | TE | RTD | Wireless | Datalink | Comments
Open/Close Pneumatic Valve | 2 |  | 1 | [8 empty] | On/Off
Modulating Pneumatic Valve | 1 |  |  |  | 1 | 1 | 1
Motor Operated Valve | 3 |  | 2 |  | 1
MCC Motor Starter | 2 | 1 | 1
Motor Feeder Swgr Breaker | 3 | 2 | 2
Main/Tie/Xfmr Feeder Swgr Breaker | 3 | 2 | 2 | [8 empty] | Medium Voltage
Switchgear Main/Tie Breaker | 2 |  | 2 | [8 empty] | Low Voltage
Instrumentation | [11 empty] | P&ID Count
Control Panel | 3 |  |  |  | 1 | [6 empty] | Common Panels: Oil water seperators, sump pumps, air compressors, SUS xfmrs, and battery/UPS
PLC Interface | 10 |  | 4 |  | 4 |  | 2 |  |  |  |  | Common PLC interface: CEMS, Aux Boiler, Water Treatment, duct burner, diverter damper, FG compressor, Switchyard, and GSU/UAT xfmrs
Common Vendor Hardwired IO
DESCRIPTION | DI | DI_SOE | DO | DO_10A | AI | AI_HZT | AO | TE | RTD | Wireless | Datalink | Comments
HRSG | 158 |  | 76 |  | 62 | 4 | 20 | 118 |  |  |  | Heat Recovery Steam Generator
CT | 19 | 2 | 27 |  | 11 |  | 6 |  |  |  |  | Combustion Turbine
ST | 30 | 5 | 26 |  | 8 |  | 3 | 1 |  |  |  | Steam Turbine
SCR | 7 |  | 3 |  | 4 |  | 1 | 10 |  |  |  | Selective Catalytic Reduction

## Signal Philosophy
Device Type | I/O |  | Command | Signal Type | Action / Function | KPE Tag
Open/Close (On/Off) Pneumatic Valve | Digital | Output | Maintained | Maintained output | Open or close (depends on fail state of the valve) | uu-FY/HY/LY/PY/TY-yyyzzz (see note 1)
| Digital | Input | Maintained | Normally open | Limit switch closed when fully open | uu-ZSO-yyyzzz
| Digital | Input | Maintained | Normally open | Limit switch closed when fully closed | uu-ZSC-yyyzzz
Modulating Pneumatic Valve | Analog | Output | n/a | 4-20 mA | 0 to 100% demand | uu-FY/LY/PY/TY-yyyzzz (see note 1)
| Analog | Input | n/a | HART variable (when feedback is for indication only) 4-20 mA (when feedback is required for control) | 0 to 100% position | uu-HZT-yyyzzz for HART uu-ZT-yyyzzz for hardwired
| Digital | Input | Maintained | Normally open | Limit switch closed when fully closed (only used for a few applications such as bypass and bypass spray valves) | uu-ZSC-yyyzzz
Motor Operated Valve | Digital | Output | Maintained | Maintained output | Open | uu-HYH-yyyzzz
| Digital | Output | Maintained | Maintained output | Close | uu-HYL-yyyzzz
| Digital | Input | Maintained | Normally open | Limit switch closed when fully open | uu-ZSO-yyyzzz
| Digital | Input | Maintained | Normally open | Limit switch closed when fully closed | uu-ZSC-yyyzzz
| Digital | Input | Maintained | Normally open (closed when ready) | Ready | uu-YS-yyyzzz
| Analog | Input | n/a | 4–20 mA | 0 to 100% position (only used for valves that need to be jogged in an intermediate position) | uu-ZT-yyyzzz
MCC Motor Starter | Digital | Output | Maintained | Maintained output | Run | uu-HY-yyyzzz
| Digital | Input | Maintained | Normally open (closed when running) | Motor running | uu-YS-yyyzzzA
| Digital | Input | Maintained | Normally closed (open to alarm) | Ready indication | uu-YS-yyyzzzB
| Digital (SOE) | Input |  | Normally open (close to alarm) | Tripped | uu-YS-yyyzzzC
Motor Feeder Switchgear Breaker | Digital | Output | Momentary | Momentary output | Start | uu-HYH-yyyzzz
| Digital | Output | Momentary | Momentary output | Stop | uu-HYL-yyyzzz
| Digital | Input | Maintained | Normally open (closed when running) | Motor running | uu-YS-yyyzzzA
| Digital | Input | Maintained | Normally open (close to alarm) | Alarm from multifunction relay | uu-YS-yyyzzzB
| Digital | Input | Maintained | Normally open (closed when racked in) | Breaker in test position | uu-YS-yyyzzzC
| Digital (SOE) | Input | Maintained | Normally open (close to alarm) | LOR tripped | uu-YS-yyyzzzD
| Digital (SOE) | Input | Maintained | Normally open (close to alarm) | Protection relay operated | uu-YS-yyyzzzE
Main/Tie/Xfmr Feeder Switchgear Breaker (Medium Voltage) | Digital | Output | Momentary | Momentary output | Breaker close | uu-HYH-yyyzzz
| Digital | Output | Momentary | Momentary output | Breaker open | uu-HYL-yyyzzz
| Digital | Input | Maintained | Normally open | Breaker closed | uu-ZSC-yyyzzz
| Digital | Input | Maintained | Normally open (close to alarm) | Alarm from multifunction relay | uu-YS-yyyzzzB
| Digital | Input | Maintained | Normally open (closed when racked in) | Breaker in test position | uu-YS-yyyzzzC
| Digital (SOE) | Input | Maintained | Normally open (close to alarm) | LOR tripped | uu-YS-yyyzzzD
| Digital (SOE) | Input | Maintained | Normally open (close to alarm) | Protection relay operated | uu-YS-yyyzzzE
Switchgear Main/Tie Breaker (Low Voltage) | Digital | Output | Momentary | Momentary output | Breaker close | uu-HYH-yyyzzz
| Digital | Output | Momentary | Momentary output | Breaker open | uu-HYL-yyyzzz
| Digital | Input | Maintained | Normally open | Breaker closed | uu-ZSC-yyyzzz
| Digital | Input | Maintained | Normally open (close to alarm) | Alarm from multifunction relay | uu-YS-yyyzzzB
Instrumentation | Analog | Input | n/a | 4-20 mA | Transmitters | uu-FT/LT/PT/PDT/TT/VT-yyyzzz (see note 2)
| Analog | Input | n/a | 4-20 mA | Analyzers | uu-AT-yyyzzz
| Analog | Input | n/a | 4-20 mA | Energy monitors | uu-ET/IT/JT-yyyzzz (see note 2)
| Analog | Input | n/a | mV | Thermocouples | uu-TE-yyyzzz
| Analog | Input | n/a |  | RTDs | uu-TE-yyyzzz
| Digital | Input | Maintained | Normally open for indication only Normally closed for alarm | Process switches | uu-FSL/LSL/PSL/PDSL/TSL-yyyzzz uu-FSLL/LSLL/PSLL/TSLL-yyyzzz uu-FSH/LSH/PSH/PDSH/TSH/VSH-yyyzzz uu-FSHH/LSHH/PSHH/TSHH/VSHH-yyyzzz (see note 2)
Notes
1 | First letter to be determined based upon process variable used to control the valve. HY to be used for devices that are not directly controlled a process variable. These devices are usually valves that are manually opened and closed from the DCS. See ISA S5.1 for additional information.
2 | First letter to be determined based upon ISA S5.1. If a transmitter is to be purchased with a display for local indication, FIT/LIT/PIT/PDIT/TIT/VIT should be used to indicate the local indication.