## SPEC 94.03.06.100 - Battery
Project:
KED #:
Revision:
Date:
TECHNICAL SPECIFICATION 853/94.03.06.100
Battery and Chargers
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of a 125 VDC Station Battery system in accordance with this specification and stated Standards.
1 | DC System General Requirements
1.01 | Nominal Voltage, Volts DC, ungrounded | 125
1.02 | Equalize Charging Voltage, Volts DC | 140
1.03 | Float Charging Voltage, Volts DC | 135
1.04 | Minimum End-of-Discharge Voltage, Volts DC | 105
2 | Battery
2.01 | Number of Cells | 60
2.02 | Cell Type | Flooded Lead-Calcium
2.03 | Electrolyte Specific Gravity @ 77°F, Cell Fully Charged | 1.215
2.04 | Battery Duty Cycle
2.05 | Period 1
2.06 | Duration (minutes)
2.07 | Load (Amps)
2.08 | Period 2
2.09 | Duration (minutes)
2.1 | Load (Amps)
2.11 | Period 3
2.12 | Duration (minutes)
2.13 | Load (Amps)
2.14 | Period 4
2.15 | Duration (minutes)
2.16 | Load (Amps)
2.17 | Battery Service Life, Years | 20
2.18 | Age Compensation Factor | 1.25
2.19 | Installation Location Average Ambient Temperature (°F) | 77 |  |  |  | Engineer to confirm
2.2 | Temperature Compensation Factor | 1
2.21 | Design Margin | 10%
3 | Battery Chargers
3.01 | Number of 100% Capacity Chargers | 2
3.02 | Maximum Recharge Time
3.03 | With one charger
3.04 | With two chargers
3.05 | Input Voltage, VAC, three-phase | 480
3.06 | Input Circuit Breaker Short-Circuit Rating | 65kA symmetrical rms
3.07 | Normal Expected Continuous Load (Amps)
3.08 | Capable of Operation Disconnected From Battery (Battery Eliminator) | Yes
3.09 | Minimum Efficiency | 90%
3.1 | Switch Selectable Charging Voltage, Float/Equalize | Yes
3.11 | Output Voltage Adjustment, Float or Equalize | +/-5%
3.12 | Output Voltage Regulation (+/-10% input volts, +/-5% frequency) | +/-1%
3.13 | Current Limit of Full Load Current | 125%
3.14 | Ripple, % RMS | <2%
3.15 | Charger DC Output, 2-pole Circuit Breaker | Required
3.16 | Equalizing Timer on Panel Front, 0-100 Hours, Manual Start | Required
3.17 | Float and Equalize Voltage Potentiometers | Required
3.18 | DC Ground Detection Relay, 10k ohm Sensitivity | Required
3.19 | Input AC Voltmeter, Output DC Voltmeter and Ammeter, 2% Accuracy | Required
3.2 | Charger Enclosure Color | ANSI 61 Gray
3.21 | Charger Enclosure Rating | NEMA 1
4 | Battery Rack and Accessories
4.01 | Rack Configuration | 2-Tier
4.02 | Rack Fabrication Material | Steel
4.03 | All Cell Interconnecting Hardware, incl. links, inter-step connectors, plates | Required
4.04 | One Hydrometer | Required
4.05 | One Thermometer | Required
4.06 | One Cell Lifting Strap and Spreader | Required
4.07 | Four 16 oz. Cans of NO-OX-ID "A" Grease | Required
4.08 | One Lot Adhesive Cell Numbers | Required
4.09 | One battery room safety kit, w/ goggles, emergency eye wash, soda, gloves, apron, polycarbonate face shield, etc. | Required
4.1 | One lot necessary wrenches for cell hardware | Required
4.11 | One DC rated 2-pole non-fused battery disconnect in indoor rated NEMA 1 enclosure for battery isolation | Required
4.12 | Two DC rated 2-pole non-fused 400A disconnects in outdoor NEMA 4 enclosures | Required
4.13 | Stainless Steel Spill Containment System | Required
4.14 | Battery Monitoring System (BMS)
4.15 | Measurements: battery voltage, string currents, cell/block voltages, ambient and battery temperatures, cell/string impedance
4.16 | Calculates: discharge time remaining, depth of discharge, and performance index
4.17 | Logs: battery discharges, alarms, events, daily max and mins
4.18 | Features: expandable architecture, accommodate min of 62 cells, function keys with keypad, LCD display, network port
5 | DC Power Panel(s)/Switchboard(s)
5.01 | Quantity
5.02 | Bus Rating (MLO), Amps (Ungrounded Supply)
5.03 | Short-Circuit Capability | As Required+10% Margin
5.04 | Quantity of Two-Pole Positions
5.05 | Enclosure Rating | NEMA 1
6 | Spare Parts
6.01 | One (1) Set of Spare Fuses of Each Size and Type Used in the Equipment | Not Required
6.02 | One (1) Set of Spare Lamps for all Lamps Used | Not Required
6.03 | One Spare Breaker of Each Size Used | Not Required
6.04 | One Set of Spare Meters | Not Required
6.05 | Manufacturer Recommended Start-Up Spare Parts | Required
6.06 | Manufacturer Recommended Two-Year Spare Parts | Not Required
7 | Drawings Supplied as part of this Specification
7.01 | Installation Location Arrangement Drawing
7.02 | DC System One-Line Diagram
8 | Data to be supplied by Vendor
8.01 | Battery
8.02 | Manufacturer
8.03 | Type of Cell
8.04 | Cell Quantity
8.05 | Amp-hour Capacity
8.06 | Assembled Battery/Battery Rack Weight, lbs
8.07 | Assembled Battery/Battery Rack Dimensions (LxWxH), inches
8.08 | Battery Charger(s)
8.09 | Manufacturer and Model
8.1 | DC Output Current Rating, Amps
8.11 | Dimensions, inches
8.12 | Charger Weight, lbs
8.13 | 125 VDC Panelboard/Switchboard
8.14 | Manufacturer and Model
8.15 | Dimensions (LxWxH), inches
8.16 | Weight, lbs
8.17 | Training and Start-up Supervision
8.18 | Unit Rates ($/Man Hour)
8.19 | Expenses, meals, lodging, auto, travel included
8.2 | Recommended Erection Assistance (8hr Days)
8.21 | Recommended Training Period (8hr Days)
9 | Additional Comments
9.01
Note on B21: Cell Type: If VRLA is specified then a Battery Monitoring System (BMS) is mandatory and must be specified. See below.
Note on C21: Choose flooded lead-calcium unless EPC contract has other requirement.
Note on B23: Battery Duty Cycle: Add/delete periods as required. Based on EPC requirements and equipment used on project.
Note on C38: Base on contract HVAC requirements, if any, for interior spaces. 77° results in no temperature correction factor with lead-acid batteries and smallest battery.
Note on C45: Recharge Time: Base on contract requirements. If none, use 24 hours.
Note on C46: Recharge Time: Base on contract requirements. If none, use 24 hours.
Note on C49: Continuous Load: This is the continuous DC load the charger would be serving while simultaneously recharging the battery.
Note on C79: Battery Monitoring System: Required only if using VRLA battery or required by the contract