## SPEC 854 - UPS
Project:
KED #:
Revision:
Date:
SPECIFICATION 94.03.06.125
120 VAC Uninterruptible Power System
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of a 120 VAC Uninterruptible Power System in accordance with this specification and stated Standards. Site parameters can be found in additional attachments.
1 | Inverter and System Requirements
1.01 | Quantity | One (1)
1.02 | Unit Rating, kVA (at 1.0 pf)
1.03 | Inverter Type | PWM or Ferro |  |  |  | PWM is recommended
1.04 | Output Nominal Voltage, Volts AC | 120
1.05 | Minimum Input Voltage, Volts DC | 105
1.06 | Maximum Input Voltage, Volts DC | 140
1.07 | Output Voltage Regulation, Load Power Factor of 0.8 to 1.0 | +/- 2.0%
1.08 | Output Frequency Regulation | +/- 0.1%
1.09 | Efficiency, at Rated Load | 83-88%
1.1 | Harmonic Distortion | <5% THD
1.11 | Overload Capacity for 30 seconds, without bypass source | 150%
1.12 | Overload Capacity for 10 minutes, without bypass source | 125%
2 | Additional Items
2.01 | Integral Static Transfer Switch | Included
2.02 | Input with 1 pole breaker, 35kAIC minimum; Zero Transfer Time; 100-125% Adjustable Overcurrent Transfer Capacity; 1000% Overload Capacity (1-cycle); Sync Supervised.
2.03 | Integral Manual Bypass Switch | Included
2.04 | Input with 1 pole breaker, 35kAIC minimum with 600VAC Rotary Drum; Make Before Break Switching with Zero Transfer Time; Sync Supervised; Continuous Operation at 125% of Rated Full Load; 1000% Overload Capacity (1-cycle)
2.05 | Inverter Enclosure Rating | NEMA 1
2.06 | UPS System Enclosure Finish | Manufacturer's Standard
2.07 | UPS System Alternate Power Source | Included
2.08 | Shielded Isolation Transformer, Dry Type, 150°C Rise, Copper Windings, 45dBA Sound Level, 4x2.5% Taps, Indoor Enclosure, Floor Mounted, kVA capacity as required for specified Rating of Inverter
2.09 | Transformer Type | Regulating
2.1 | UPS System Alarms and Indications
2.11 | Lighted Mimic Panel w/ Graphic Block Diagram (Includes indicators for Battery Supplying Load, Bypass Source Failure, Fan Failure, Inverter Failure, Low DC Disconnect, Inverter in Sync, Inverter Supplying Load, Bypass Supplying Load) | Included
2.12 | Common Alarm Output Relay | Included
2.13 | System Meters
2.14 | Voltmeters: AC Output, DC Input, Bypass Source Input | Included
2.15 | Ammeters: AC Output, DC Input, Bypass Source Input | Included
2.16 | Frequency Meter: AC Output | Included
3 | UPS Power Panel(s)
3.01 | Quantity | See One Line
3.02 | Rating of Panel Bus (MLO), Amps | As Required+10% Margin
3.03 | Number of Single Pole Positions | See One Line
3.04 | Outgoing Feeder Protective Devices, 10kAIC | Fused Switches
3.05 | Enclosure Rating | NEMA 1
4 | Spare Parts
4.01 | One (1) Set of Spare Fuses of Each Size and Type Used in the Equipment | Required
4.02 | One (1) Set of Spare Lamps for all Lamps Used | Required
4.03 | One Spare Breaker of Each Size Used | Not Required
4.04 | One Set of Spare Meters | Not Required
4.05 | Manufacturer Recommended Start-Up Spare Parts | Required
4.06 | Manufacturer Recommended Two-Year Spare Parts | Not Required
5 | Codes and Standards
5.01 | Follow All the Latest Applicable Standards and Codes Including but Not Limited To
5.02 | American National Standards Institute (ANSI)
5.03 | American Society of Testing and Materials (ASTM)
5.04 | Canadian Electrical Code (CEC) | N/A
5.05 | Canadian Standards Association (CSA) | N/A
5.06 | Institute of Electrical and Electronic Engineers (IEEE)
5.07 | IEEE C37.90.1
5.08 | IEEE C57.15
5.09 | IEEE 693
5.1 | National Electric Code (NEC)
5.11 | National Electric Safety Code (NESC)
5.12 | PB 1
5.13 | PB 1.1
5.14 | PE 1
5.15 | National Electrical Manufacturers Association (NEMA)
5.16 | NEMA TR-1
5.17 | National Fire Protection Association (NFPA)
5.18 | NFPA 70
5.19 | Underwriters Laboratories (UL)
5.2 | UL 50
5.21 | UL 1778
5.22 | Occupational Safety and Health Administration (OSHA)
5.22 | Other
6 | Drawings Supplied as part of this Specification
6.01 | Installation Location Arrangement Drawing
6.02 | UPS One-Line Diagram
7 | Data to be supplied by Vendor
7.01 | Inverter
7.02 | Manufacturer
7.03 | Inverter kVA Rating at 1.0 pf
7.04 | Enclosure Dimensions (LxWxH), inches
7.05 | Weight, lbs
7.06 | Alternate Source Transformer
7.07 | Manufacturer
7.08 | kVA Rating
7.09 | Dimensions (LxWxH), inches
7.1 | Weight, lbs
7.11 | Training and Start-up Supervision
7.12 | Unit Rates ($/Man Hour)
7.13 | Expenses, meals, lodging, auto, travel included
7.14 | Recommended Erection Assistance (8hr Days)
7.15 | Recommended Training Period (8hr Days)
8 | Additional Comments
8.01