## SPEC 890 - EDG
Project:
KED #:
Revision:
Date:
SPECIFICATION 94.03.10.125
Emergency Diesel Generator
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of Emergency Diesel Generator in accordance with this specification and stated Standards. Site parameters can be found in additional attachments.
1 | General Requirements
1.01 | Application | Outdoor
1.02 | Quantity | One (1) Unit
1.03 | Generator Standby Rating (kW) | 1500
1.04 | Generator Standby Rating (kVA) | 1875
1.05 | Power Factor | 0.8
1.06 | Generator Terminal Voltage, 3-Phase, 60 Hz (V) | 480
1.07 | Generator Connection to System | Wye to High Resistance Grounded System
1.08 | Auto-Sync Capabilities | Include
2 | Diesel Engine and Accessories
2.01 | Engine
2.02 | Engine Type | Inline or Vee-type, 4 cycle, 2 cycle not allowed
2.03 | Engine Block Machined from One (1) Casting | Included
2.04 | Gear-Type, Positive Displacement, Full Pressure Lube Oil Pump | Included
2.05 | Spray Cooled Pistons | Included
2.06 | Oil Filters, Oil Pressure Gauge, Dipstick, Oil Drain | Included
2.07 | Fuel System Component Located to Prevent Spills on Battery | Included
2.08 | Engine Accessories: Fuel, Lube Oil, Intake Air filters, Fuel Primping Pump, Service Meter, Gear Driven Water Pump | Included
2.09 | Governor
2.1 | Electronic Engine Control Module | Included
2.11 | Speed Droop 0 (isochronous) to 10%, no load to full load | Included
2.12 | Steady State Frequency Regulation | +/- 0.25%
2.13 | Provision for Remote Speed Adjustment | Included
2.14 | Load Sharing Capable | Included
2.15 | Cooling System
2.16 | Rail Mounted, Engine Driven Radiator with Blower Fan | Included
2.17 | Sized to Operate at Full Load, 85°F Ambient Air Entering Enclosure without Derating, and 50/50 Anti-Freeze Mixture | Included
2.18 | Fuel System
2.19 | Fuel Type | No. 2 Diesel
2.2 | Fuel Filter/Water Separator in addition to Fuel Filter in Fuel Inlet Line to Engine | Included
2.21 | All Fuel Piping shall be Black Iron or Flexible Fuel Hose Rated for this Service (No Galvanized), Flexible Fuel Lines Rated 300°F and 100 PSI | Included
2.22 | UL Listed, Painted Steel Sub-Base Fuel Tank with Bronze Gear Pump which Exceeds the Max Flow of Fuel Drawn by the Engine-Mounted Fuel Supply Pump, Including Fuel Return from Engine, shall be Tank Mounted and 120V | Included
2.23 | Tank Capacity at 100% of Rated Load | 24 Hours
2.24 | Tank Features
2.25 | Piping Connections for Fuel Suction/Return Lines to Tank | Included
2.26 | Fuel Supply/Return Lines to Engine | Included
2.27 | Emergency Vent | Included
2.28 | Local Fuel Fill Connections | Included
2.29 | Tank Drain Connection | Included
2.3 | Removable Inspection Plate with Gasket | Included
2.31 | Fuel Level Gauge | Included
2.32 | Steel Rupture Basin Switch | Included
2.33 | High/Low Fuel Level Switch for Remote Annuciation | Included
2.34 | UL 508 Control Module | Included
2.35 | Fuel Strainer | Included
2.36 | Exhaust System
2.37 | Exhaust Silencing System House within Enclosure | Included
2.38 | Silencer Type | Critical
2.39 | Silencer Mounted such that it's Weight not Supported by Engine Assembly | Included
2.4 | Exhaust Pipe Size Sufficient to no Exceed Engine Maximum Exhaust Backpressure | Included
2.41 | Indoor Exhaust Pipe/Muffler Laged, Max 105°F Surface Temp. | Included
2.42 | Starting System
2.43 | DC Electric Starting System with Positive Engagement | Included
2.44 | Jacket Water Heater, 120V, Single Phasem 90°F Water Temp. | Included
2.45 | Heavy Duty Lead-Acid Battery with Cables, Clamps, Minimum of 172 Amps-Hours | Included
2.46 | Battery Tray per NEC 480-7(b) with Provision for Boil-Over/Spillage and Treated to Resist Deterioration | Included
2.47 | Battery Charger: Current Limiting, Float Voltage 2.17vpc, Equalizing Voltage 2.33vpc, with Overload Protection, Rectifier, Surge Suppressor, DC Ammeter, DC Voltmeter, Fused 120 VAC Input; Annunciation for Low DC Volts, Rectifier Failure, Loss of AC High DC Volts; Amp Rating Min. 10 Amps, Wall Mounted in NEMA 1 Enclosure | Included
3 | Generator and Accessories
3.01 | Generator
3.02 | Synchronous 3-Phase Design per NEMA MG-1 | Included
3.03 | Single Bearing, Self-Ventilated, Drip Proof Design | Included
3.04 | Direct Connection to Engine Flywheel Housing with Flex Coupling | Included
3.05 | Insulation NEMA Class H | Included
3.06 | Fungus Resistant Vacuum Impregnated with Epoxy Varnish | Included
3.07 | Temperature Rise Limited to NEMA Class F | Included
3.08 | Brushless Excitation System | Included
3.09 | Permanent Magnet Type Exciter | Included
3.1 | Gen. Voltage Reg. per Automatic Voltage Regulator (AVR) | +/- 0.5%
3.11 | AVR to Include: Solid State Design, Including Electronic Voltage Buildup, Volts per Hertz Regulation, 3-Phase Sensing, Overexcitation Protection, Loss of Sensing Protection, Temperature Compensation, Voltage Overshoot on Startup Limit, Environmentally Sealed | Included
3.12 | Generator Mounted 120/240 VAC Space Heater | Included
3.13 | Remote Synchronizing Panel with the Following Features:
3.14 | Breaker Control Switch | Included
3.15 | Indicating Lights | Included
3.16 | Engine Control Switch | Included
3.17 | Ammeter Selector Switch | Included
3.18 | Voltmeter Selector Switch | Included
3.19 | Manual Synchronizing Switch | Included
3.2 | Sync Control Switch | Included
3.21 | Beckwith M3410 Generator Protection Relay | Included
3.22 | Basler BE3-27 Generator Undervoltage Relay | Included
3.23 | Basler BE3-81 Over-Frequency Relay | Included
3.24 | Ammeter | Included
3.25 | Voltmeter | Included
3.26 | Wattmeter | Included
3.27 | Power Factor Meter | Included
3.28 | Synchroscope | Included
3.29 | Synch Lamps | Included
3.3 | Interface to Woodward 2301A or Load Sharing Module (Furnished with Engine) | Included
3.31 | Woodward SPMA Automatic Synchronizer | Included
3.32 | Woodward AGLC Automatic Generator Loading Control | Included
3.33 | Basler SCP-250 Power Factor Controller | Included
3.34 | Basler RA-70A Digital Voltage Referencer Adjuster | Included
3.35 | Manual Voltage Adjusting Control Switch | Included
3.36 | Emergency Stop Pushbutton | Included
3.37 | Base Loading Control Petentiometer | Included
3.38 | Neutral Grounding Reactor and Enclosure | Included
3.39 | Mounting of Customer Supplied Remote Annunciator NFPA 110 | Included
3.4 | Generator Mounted Control Panel
3.41 | Automatic Start/Stop Operation | Included
3.42 | Adjustable Cycle Cranking | Included
3.43 | Digital Engine Monitoring | Included
3.44 | Shutdown Sensors/Alarms with Horn Reset | Included
3.45 | Adjustable Cooldown Timer | Included
3.46 | Emergency Stop Pushbutton | Included
3.47 | Self Diagnostic Capabilities | Included
3.48 | Fault Logging | Included
3.49 | Sealed against Moisture/Dirt | Included
3.5 | NEMA 1 Enclosure | Included
3.51 | Digital Readouts:
3.52 | Engine Oil Pressure | Included
3.53 | Coolant Temperature | Included
3.54 | Engine RPM | Included
3.55 | System DC Volts | Included
3.56 | Non-Resettable Engine Running Hours | Included
3.57 | Generator AC Volts | Included
3.58 | Generator AC Amps | Included
3.59 | Generator Frequency | Included
3.6 | kW meter | Included
3.61 | Meter Percent Rated Power | Included
3.62 | kVA Meter | Included
3.63 | kVAr Meter | Included
3.64 | Power Factor Meter | Included
3.65 | kWhr Meter | Included
3.66 | Indications for Protection and Diagnostics per NFPA 110 Level1:
3.67 | Low Oil Pressure | Included
3.68 | High Water Temperature | Included
3.69 | Low Coolant Level | Included
3.7 | Overspeed | Included
3.71 | Overcrank | Included
3.72 | Emergency Stop Depressed | Included
3.73 | Approaching High Coolant Temperature | Included
3.74 | Approaching Low Oil Pressure | Included
3.75 | Low Coolant Temperature | Included
3.76 | Low Battery Voltage | Included
3.77 | Control Switch not in Auto | Included
3.78 | Low Fuel Main Tank | Included
3.79 | Battery Charger AC Failure | Included
3.8 | Generator Supplying Load | Included
3.81 | Programmable Control Panel Inside Panel (Protection Relay Functions) | Included
3.82 | Remote Annunciator NFPA 110 | Included
4 | Enclosure and Misc.
4.01 | Weather Protective Enclosure (Sound Attenuated)
4.02 | Steel Weather Protective Enclosure with 14-Guage Sheet Metal | Included
4.03 | Removable Hinged Doors and End Panels | Included
4.04 | Lockable Service Access Covers for Fuel, Oil, Coolant, and Battery Access | Included
4.05 | Roof Pitched to Prevent Moisture Accumulation | Included
4.06 | Painted wit Electrostatically Applied Powder Baked Paint | Included
4.07 | Externally Mounted Emergency Stop Pushbutton | Included
4.08 | Radiator Sight Guage | Included
4.09 | Lube Oil, Coolant and Fumes Disposal Lines Terminated on Base | Included
4.1 | Interior Lighting System | Included
4.11 | Noise Reduction
4.12 | Enclosure to Provide a nominal 25 dBA Noise Reduction | Included
4.13 | Fire Detection
4.14 | Enclosure Furnished with Smoke Detector Wired to a Terminal Block for Remote Monitoring | Included
5 | Additional Items
5.01 | Generator Breaker Supplied with Generator Set | N/A
5.02 | Automatic Transfer Switch | N/A
6 | Spare Parts
6.01 | Manufacturer Recommended Start-Up Spare Parts | Required
6.02 | Manufacturer Recommended Two-Year Spare Parts | Not Required
7 | Codes and Standards
7.01 | Follow All the Latest Applicable Standards and Codes Including but Not Limited To
7.02 | American Institute of Steel Contruction (AISC)
7.03 | American National Standards Institute (ANSI)
7.04 | American Society of Testing and Materials (ASTM)
7.05 | Canadian Electrical Code (CEC) | N/A
7.06 | Canadian Standards Association (CSA) | N/A
7.07 | Institute of Electrical and Electronic Engineers (IEEE)
7.08 | National Electric Code (NEC)
7.09 | National Electric Safety Code (NESC)
7.1 | National Electrical Manufacturers Association (NEMA)
7.11 | NEMA MG 1
7.12 | NEMA MG 1-22.43
7.13 | National Fire Protection Association (NFPA)
7.14 | NFPA Standard 110
7.15 | Underwriters Laboratories (UL)
7.16 | Other
8 | Drawings Supplied as part of this Specification
8.01 | General Arrangement
8.02 | One-Line Diagram
8.03 | Equipment Layout
9 | Data to be supplied by Vendor
9.01 | Overall Dimensions (Length x Width x Height) of Enclosure
9.02 | Shipping Weight (lbs)
10 | Additional Comments
10.01