## SWBD SPEC
Project: | [6 empty] | Notes
KPE #:
Revision:
Date:
SPECIFICATION 94.03.08.200
BOP Switchboard Specification
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of low voltage switchboard. All having the ratings and accessories as specified herein. Site parameters can be found in additional attachments.
1 | Lineup General Requirements
1.01 | Lineup Name | BOP SWBD
1.02 | Installation Location | Indoors
1.03 | Installation Arrangement | See Equipment Layout
1.04 | Nominal Operating Voltage (V rms) | 480 |  |  |  |  | Engineer to enter.
1.05 | Maximum Rated Voltage (V rms) | 600
1.06 | Number of Phases/Configuration | 3-Phase, 3-Wire |  |  |  |  | 4-wire system is only applicable to solidly-grounded system that directly feed line-to-neutral loads (e.g. 277V loads on a 480V system). A 4-wire system requires a neutral bus
1.07 | Frequency (Hz) | 60
1.08 | Enclosure Rating | NEMA 1
1.09 | Color | Manufacturer's Standard
1.1 | Minimum Interrupting Current Capability (kA rms sym) | 100
1.11 | Minimum Main Horizontal Bus Ampacity (A rms) | See One-Line
1.12 | Minimum Vertical Bus Ampacity (A rms) | 300 |  |  |  |  | For normal front accesss MCCs, 300A is typical. 600A is typical for back-to-back MCCs. Fully rated vertical bus, to match the horizontal bus ampacity, is not typical and should only be used if a client req. and may limit the horizontal bus rating.
1.12 | Neutral bus (4-wire system only) | N/A
1.13 | Bus material | Tin-Plated Copper
1.17 | Incoming Line Section
1.18 | Protection Device | None - Main Lugs Only (MLO)
1.19 | Conductor Type | Cable
1.2 | Entry | Top or Bottom
1.21 | Outgoing Feeders
1.22 | Connection | Bottom Entry
1.23 | Conductor Type | Cable
1.14 | Arc-resistant Construction | Not Required
1.15 | Minimum Arcing Current Rating | N/A
1.16 | Minimum Rated Arcing Duration | N/A
1.17 | Insulating barrier to separate unit compartments from vertical bus compartment, glass reinforced polyester with cutouts | Required
1.18 | Automatic Shutters | Required
1.19 | Copper ground bus extending full length of Switchboard | Required
1.2 | Wiring Method | NEMA Class I Type B
1.21 | Insulated Horizontal and Vertical Busbars | Required
1.22 | Vertical bus isolation barrier | Required
1.23 | Each unit equipped with side-mount pull-apart terminal blocks rated 600V | Required
1.24 | Padlocking facilities to allow locking the disonnect in OFF position with up to three padlocks with door open or closed | Required
1.25 | Metering
1.26 | Incomer: Microprocessor based three-phase power monitor displaying phase currents, voltage, L-L, L-N, power-real and reactive apparent, power factor, frequency, energy: watthours, var hours VA hours (on MCC incomer section w/ necessary instrument transformers) (meter to have Mod Bus communication capability), including any required VTs and CTs | Not Required
1.27 | Door mounted microprocessor based meter as described above in smaller format for mounting on individual starter/units | Not Required
2 | Power Circuit Breaker Requirements
2.01 | Standard(s) - Latest Revision | IEEE C37.13, C37.16, C37.17, C37.20.1
2.02 | Interrupter Insulating Medium | Air
2.03 | Removal | Horizontal Drawout
2.04 | Maximum Rated Interrupting Time (Cycles) | Manufacturer's Standard
2.05 | Maximum Rated Closing Time (Cycles) | Manufacturer's Standard
2.06 | Molded Case Breaker Quantities
2.07 | 20A | See Load List
2.08 | 30A | See Load List
2.09 | 50A | See Load List
2.1 | 70A | See Load List
2.11 | 80A | See Load List
2.12 | 100A | See Load List
2.13 | 125A | See Load List
2.14 | 150A | See Load List
2.15 | 175A | See Load List
2.16 | 200A | See Load List
2.17 | 225A | See Load List
2.18 | 250A | See Load List
2.19 | Trip Coil Monitoring | Not Required
3 | Options
3.01 | Ground bus in each vertical wireway | Required
3.02 | Ground fault relays on all outgoing motor and breaker feeds | Not Required
3.03 | Vendor to reserve one vertical section for installation by Vendor of Purchaser furnished PLC or DCS I/O rack | Not Required
3.04 | Remote Racking | Not Required
4 | Spare Parts
4.01 | Power Fuses, Two (2) of Each Size, if applicable | Not Required
4.02 | Pilot Lights, Five (5) Spare of Each Color | Not Required
4.03 | Control Circuit Fuses, Two (2) Each of CPT Primary Fuses | Not Required
4.04 | Control Circuit Fuses, Two (2) Each of CPT Secondary Fuses | Not Required
4.05 | Two (2) spare contactors of each size used | Not Required
4.06 | Two (2) spare breakers or motor circuit protectors of each size | Not Required
4.07 | One (1) spare of each size starter | Not Required
4.08 | One Quart Touch Up Paint | Required
4.09 | Manufacturer Recommended Start-Up Spare Parts | Required
4.1 | Manufacturer Recommended Two-Year Spare Parts | Not Required
5 | Drawings Supplied as part of this Specification
5.01 | General Arrangement | Not Included
5.02 | Electrical One-Line | Included
5.03 | Equipment Layout | Included
5.04 | Typical Schematics | Not Included
6 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
6.01 | Outline/General Arrangement with overall dimensions, NTE weights, anchorage requirements | 6
6.02 | Electrical One-Line and Three-Line Diagram | 6
6.03 | Typical Schematics including terminal numbers | 6
6.04 | Heat rejection data | 6
6.05 | Seismic Certification (if applicable) | 8 |  |  |  | Engineer to determine applicability
6.06 | O&M Manuals - Standard 3-ring binder (follow enclosure contract schedule if purchased under the same contract) | 4 weeks after delivery
6.07 | # of Proof copies required - 4 | N/A
6.08 | # of Final copies required - 8 | N/A
6.09 | # of CD's required - 8 | N/A
6.1 | Special O&M Manual requirements - None | N/A
7 | Additional Data to be supplied by Bidder
7.01 | Overall Dimensions (Length x Width x Height)
7.02 | Total Weight (lbs)
7.03 | Shipping Weight (lbs)
8 | Additional Requirements
8.01
Note on B72: Select Required if 480V system is solidly-grounded; select Not Required otherwise