## SPEC 820 - Electrical Enclosure
Project: | [6 empty] | Notes
Revision:
Date:
SPECIFICATION 94.03.08.100 | [6 empty] | 1.1Low voltage (≤ 600V) switchgears shall be provided with a traveling breaker lifting hoist. Seller shall show hoist space requirements on building’s general arrangement, conduit, and tray layout plans.
Electrical Enclosure | [6 empty] | 4x4x4 pull stations?
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of the Electrical Enclosure(s) in accordance with this specification and stated Standards. Site parameters can be found in additional attachments.
1 | General Requirements
1.01 | Application | Outdoor
1.02 | Quantity | See Enclosure Layouts
1.03 | Minimum Interior Length | Per Equipment Layout Drawing
1.04 | Minimum Interior Width | Per Equipment Layout Drawing
1.05 | Minimum Interior Height | 10 FT
1.06 | Shipping splits
1.07 | Medium Voltage Enclosure | 2
1.08 | Essential Services Enclosure | 2
1.09 | HRSG Enclosure | 1
1.1 | Cooling Tower Enclosure | 1
2 | Construction Requirements
2.01 | Enclosure shall be anchored to and supported by:
2.02 | Medium Voltage Enclosure | Stilts | By Contractor |  |  |  | If stilts, verify Structural is carrying support steel
2.03 | Essential Services Enclosure | Stilts | By Contractor
2.04 | HRSG Enclosure | Stilts | By Contractor
2.05 | Cooling Tower Enclosure | Stilts | By Contractor
2.06 | Heavy Structural Steel Enclosure Base, Rigidly Braced
2.07 | Welded Perimeter Beam Construction, Skid Type | Not Included
2.08 | Structural Steel Angle Iron Supports | Not Included
2.09 | Removable Lifting Lugs | Not Included
2.1 | Floor shall be 1/4" Steel Plate Welded to Base & Perimeter | Included
2.11 | Floor Covering shall be Durable Non-Skid Gray Floor Enamel | Included
2.12 | Floor Penetrations with Surface Mounted Covers | Included
2.13 | Roof (Peak 3" per 15' to Shed Water)
2.14 | Painted Aluminum Gutter & Downspouts | Included
2.15 | Roof Penetrations with Weathertight Seals | Included
2.16 | Design Roof Loading (lbs per square foot) | See Section 1B
2.17 | Walls | [5 empty] | fire rated?
2.18 | Exterior Panels shall be 18 Guage Galvanized Steel | Included
2.19 | Interior Panels shall be 16 Guage Galvanized Steel | Included
2.2 | Wall Penetrations with Weathertight Seals | Included
2.21 | Design Wind Loading (MPH) | See Section 1B
2.22 | Minimum Insulation
2.23 | Wall Insulation | R-11
2.24 | Ceiling Insulation | R-19
2.25 | Floor Insulation | R-8
2.26 | Doors
2.27 | Material | 14 Guage Galvanized Steel
2.28 | Features
2.29 | Panic Door Hardware | Included
2.3 | Auto Closer | Included
2.31 | Hold-Open Alarm | Included
2.32 | Viewing Window | Included
2.33 | Key Lock | Included
2.34 | Exterior Rain Canopies | Included
2.35 | Double Wide doors shall be 6' W x 8' H | Included
2.36 | Single Wide doors shall be 4' W x 8' H | Included
2.37 | Rear Access Doors for Installed Equipment | Included
2.38 | Paint Finish
2.39 | Roof & Walls, Interior & Exterior | Polyester Powdercoat
2.4 | Floor, Exterior | Epoxy Mastic Undercoat
2.41 | Floor Interior | Non-Skid Paint
2.42 | Battery Room Floor, Interior | Acid Resistant Epoxy Coating
2.43 | Battery Rack | Acid Resistant Epoxy Coating
3 | Accessories
3.01 | Lighting
3.02 | Minimum Illumination Level | 35 Foot Candles at Floor Level
3.03 | Electric Fluorescent Fixtures, 120VAC, 2-32 Watt | Included
3.04 | Exterior Light, 70 Watt HPS, Photocell Activated, at Each Door | Included
3.05 | Interior Exit & Emergency Light Fixtures | Included
3.06 | Three Way Light Switches at Each Door | Included
3.07 | Receptacles, Duplex 120VAC, 20A, GFCI
3.08 | Two (2) Interior GFCI Receptacles | Included
3.09 | Two (2) Exterior GFCI Receptacles | Included
3.1 | 60A Welding Receptacle with integral disconnect mounted and wired to external module wall prior to shipment | Included |  |  |  | Include if the building is on stilts. Exclude otherwise
3.11 | Fire Protection
3.12 | Fire Extinguishers, CO2, 20 lbs., Rated B-C Fire Class | Included
3.13 | Two (2) Smoke Detectors with Auxiliary Contacts | Included
3.14 | Manual Pull Fire Alarm Station | Included
3.15 | Building Service Transformer
3.16 | Size | 45 kVA, 3 Ph, 480-208/120VAC
3.17 | Vibration-Isolating Mounting | Included
3.18 | Panelboard
3.19 | One (1) 480V, 225A, 3 Ph, 3 Wire, 36 Pole Panelboard | Included
3.2 | Two (2) 208/120V, 225A, 3 Ph, 3 Wire, 42 Pole Panelboard | Included
3.21 | HVAC
3.22 | Minimum Indoor Temperature (Degree F) | 58
3.23 | Maximum Indoor Temperature (Degree F) | 78
3.24 | Adjustable Thermostat | Included
3.25 | Supply Power | 480VAC, 3 Ph
3.26 | Battery Room (For Contractor Supplied DC Battery)
3.27 | Dual Battery Room Vent Fans | Included
3.28 | Safety Shower | Included
3.29 | Room Classified Class 1 Div 2 | Included
3.3 | Grounding System | [5 empty] | 1.1Electrical Equipment Enclosure shall be provided with a minimum 4/0 AWG, bare copper, interior perimeter ground conductor (bus bar). The perimeter ground conductor shall be bonded to the perimeter base structural steel in two (2) places. If the enclosure is split, two (2) grounding points shall be provided on each split. All interior electrical equipment shall be bonded to the ground conductor.
3.31 | Silver Plated Copper Ground Loop, 1/4" x 2" | Included
3.32 | Stainless Steel Ground Pads on Diagonal Building Corners | Included
3.33 | Each Equipment Ground Bus Connected to Building Ground | Included
4 | Installation & Wiring of Buyer Provided Equipment | [5 empty] | 1.1.1 Large power wiring and DCS cabling across a shipping split shall be routed and terminated at the factory prior to splitting the shipping splits for shipment. This wiring shall then be un-terminated and coiled up in the cable tray for re-connection by the Contractor in the field.
4.01 | Medium Voltage Switchgear & Motor Control Center | Included
4.02 | Low Voltage Switchgear | Included
4.03 | Low Voltage Motor Control Center | Included
4.04 | DCS Wiring | Included
4.05 | Battery System | Included
4.06 | UPS Equipment | Included
4.07 | Non-Seg Bus with Weathertight Seal | Included
4.08 | Number of Terminations | See Bid Form
5 | Additional Items
5.01 | Plant Battery System Safety Accessories
5.02 | Stainless Steel Drip Pan with Floor Drain | Install Only
5.03 | Eye Wash & Bowl | Included
5.04 | Emergency Shower | Included
5.05 | PPE Cabinet | Included
6 | Spare Parts
6.01 | One Gallon Exterior Paint | Required
6.02 | One Gallon Interior Paint | Required
6.03 | One Gallon Non-Skid Floor Paint | Required
6.04 | Manufacturer Recommended Start-Up Spare Parts | Required
6.05 | Manufacturer Recommended Two-Year Spare Parts | Not Required
7 | Codes and Standards
7.01 | Follow All the Latest Applicable Standards and Codes Including but Not Limited To
7.02 | American Institute of Steel Contruction (AISC)
7.03 | American National Standards Institute (ANSI)
7.04 | American Society of Testing and Materials (ASTM)
7.05 | Canadian Electrical Code (CEC) | N/A
7.06 | Canadian Standards Association (CSA) | N/A
7.07 | Institute of Electrical and Electronic Engineers (IEEE)
7.08 | National Electric Code (NEC)
7.09 | National Electric Safety Code (NESC)
7.1 | National Electrical Manufacturers Association (NEMA)
7.11 | NEMA ST-20 Dry Type Transformer for General Applications
7.12 | National Fire Protection Association (NFPA)
7.13 | Underwriters Laboratories (UL)
7.14 | 489 Molded-Case Breakers and Circuit Breaker Enclosures
7.15 | 506 Special Transformers
7.16 | 943 Ground-Fault Circuit Interrupters
7.17 | Other
8 | Drawings Supplied as part of this Specification
8.01 | Site General Arrangement | Not Included
8.02 | One-Line Diagram | Included
8.03 | Module and Equipment Layout | Included
9 | Data to be supplied by Vendor
9.01 | Interior Length
9.02 | Interior Width
9.03 | Interior Height
9.04 | Bill of Materials
9.05 | Shipping Weight (lbs) (with all Equipment)
10 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
10.01 | O&M Manuals - Standard 3-ring binder | 4 weeks after delivery
10.02 | # of Proof copies required - 4 | N/A
10.03 | # of Final copies required - 8 | N/A
10.04 | # of CD's required - 8 | N/A
10.05 | Special O&M Manual requirements - None | N/A
10.06 | Outline with overall dimensions, NTE weights, foundation requirements | 6
10.07 | Final Layout dwgs | 12
10.08 | Building electrical drawings - includes lighting layouts, panelboard schedules, wiring diagrams, circuit and termination schedule for building wiring | 12
10.09 | PE Stamped structural drawings (if required) | 16 |  |  |  | Engineer to verify requirement
10.1 | PE Stamped HVAC and lighting drawings (if required) | 8 |  |  |  | Engineer to verify requirement
11 | Testing requirements
11.01 | Minimum number of factory acceptance tests per module | One
11.02 | Expected duration of each acceptance test | 2 Days
11.03 | Basic tests to include Seller is expected to support:
11.04 | Continuity test on all control cables with required documentation | Include
11.05 | Seller to apply voltage and function test all installed equipment | Include
11.06 | Point to Point wire checks including termination pull test to ensure cables are landed securely | Include
11.07 | Megger test of all MV and LV buses assembled at the PDC supplier location - include documentation | Include
11.08 | Megger test of any MV cable installed by supplier - include documentation | Include
12 | Typical Payment Milestones
12.01 | Upon approval of engineering deliverables for all major equipment being supplied | 10%
12.02 | Upon submittal of unpriced purchase orders for major equipment | 20%
12.03 | Upon Seller's receipt of Contractor's release for fabrication | 10%
12.04 | Upon proof of Seller's receipt of major equipment to PDC Supplier | 20%
12.05 | Upon complete delivery and acceptance of PDC and loose shipped equipment to project site | 35%
12.06 | Upon Contractor approval of final O&M manuals and all outstanding engineering deliverables | 5%
13 | Expected Delivery | 10 months after NTP for first module - subsequent modules every two weeks afterwards
14 | Additional Comments
14.01 | Engineer to fill in for: LED lighting, additional fire walls, including platforms, etc