## SPEC 94.03.08.125.03B - LVMCC
Project: | [6 empty] | Notes
KED #:
Revision:
Date:
SPECIFICATION 821B/94.03.08.125.03B
Low-Voltage Motor Control Centers
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of 480V Motor Control Centers having the ratings and accessories as specified herein.
1 | Lineup General Requirements
1.01 | Lineup Name | See Load List
1.02 | MCC Tag | See One-Line
1.03 | Installation Location | Indoors in Pre-Package Enclosure |  |  |  |  | Engineer to enter.
1.04 | Installation Arrangement | See Equipment Layout
1.05 | Nominal Rated Voltage (V rms) | 480
1.06 | Maximum Rated Voltage (V rms) | 600
1.07 | Number of Phases/Configuration | 3-Phase 3-Wire |  |  |  |  | 4-wire system is only applicable to solidly-grounded system that directly feed line-to-neutral loads (e.g. 277V loads on a 480V system). A 4-wire system requires a neutral bus
1.08 | Frequency (Hz) | 60
1.09 | Enclosure Rating | NEMA 1
1.1 | Color | Manufacturer's Standard
1.11 | Minimum Interrupting Current Capability (kA rms symmetrical) | 100
1.12 | Minimum Withstand Time for Short-Circuit Current (cycles) | 10
1.13 | Minimum Main Horizontal Bus Ampacity (A rms) | See Load List
1.14 | Minimum Vertical Bus Ampacity (A rms) | 300 |  |  |  |  | For normal front accesss MCCs, 300A is typical. 600A is typical for back-to-back MCCs. Fully rated vertical bus, to match the horizontal bus ampacity, is not typical and should only be used if a client req. and may limit the horizontal bus rating.
1.15 | Neutral bus (4-wire system only) | N/A
1.16 | Bus material | Tin-Plated Copper
1.17 | Incoming Line Section
1.18 | Protection Device | None - Main Lugs Only (MLO)
1.19 | Conductor Type | Cable
1.2 | Entry | Top or Bottom
1.21 | Outgoing Feeders
1.22 | Connection | Top and Bottom Entry
1.23 | Conductor Type | Cable
1.21 | Arc-resistant Construction | Not Required
1.22 | Minimum Arcing Current Rating | N/A
1.23 | Minimum Rated Arcing Duration | N/A
1.24 | Insulating barrier to separate unit compartments from vertical bus compartment, glass reinforced polyester with cutouts | Required
1.25 | Automatic Shutters | Required
1.26 | Copper ground bus extending full length of MCC | Required
1.27 | Wiring Method | NEMA Class I Type B
1.28 | Insulated Horizontal and Vertical Busbars | Required
1.29 | Vertical bus isolation barrier | Required
1.3 | Each unit equipped with side-mount pull-apart terminal blocks rated 600V | Required
1.31 | Padlocking facilities to allow locking the disonnect in OFF position with up to three padlocks with door open or closed | Required
1.32 | Metering
1.33 | Incomer: Microprocessor based three-phase power monitor displaying phase currents, voltage, L-L, L-N, power-real and reactive apparent, power factor, frequency, energy: watthours, var hours VA hours (on MCC incomer section w/ necessary instrument transformers) (meter to have Mod Bus communication capability), including any required VTs and CTs | Not Required
1.34 | Door mounted microprocessor based meter as described above in smaller format for mounting on individual starter/units | Not Required
2 | Motor Controller and Contactor Requirements
2.01 | Method of short circuit protection (adjustable) | Motor Circuit Protector/Circuit Breaker
2.02 | Starter unit | Withdrawable
2.03 | Overload Relays, Three Phase, adjustable (if specified to be bimetallic, furnish with interchangeable heaters) | Solid-State Adjustable
2.04 | Spare Auxiliary Contacts Required | 2 NO and 2 NC
2.05 | Control Power Transformers, Single Phase, Voltage Ratio of 480/120, Minimum Rating of 150VA for Size 1 and 2, 300VA for Sizes 3 and Higher | Required
2.06 | "Hand-Off-Auto" switches | Not Required
2.07 | Red "Run/On" and Green "Stopped/Off" lamps + additional lights for any 2-speed or reversing starters | Required
3 | Quantity Buildup
3.01 | Motor Starters
3.02 | Full-Voltage Non-Reversing (FVNR)
3.03 | Size 1 (10hp) | See Load List
3.04 | Size 2 (25hp) | See Load List
3.05 | Size 3 (50hp) | See Load List
3.06 | Size 4 (100hp) | See Load List
3.07 | Size 5 (200hp) | See Load List
3.08 | Size 6 (400hp) | See Load List
3.09 | Full-Voltage Reversing (FVR)
3.1 | Size 1 (10hp) | See Load List
3.11 | Size 2 (25hp) | See Load List
3.12 | Full-Voltage 2-Speed (2-Winding)
3.13 | Size 4 (100hp) | See Load List
3.14 | Size 5 (200hp) | See Load List
3.15 | Size 6 (400hp) | See Load List
3.16 | Integral Variable Frequency Drive (VFD)
3.17 | Size 1 (10hp) | See Load List
3.18 | Size 2 (25hp) | See Load List
3.19 | Size 3 (50hp) | See Load List
3.2 | Size 4 (100hp) | See Load List
3.21 | Size 5 (200hp) | See Load List
3.22 | Size 6 (400hp) | See Load List
3.23 | Size 7 (600hp) | See Load List
3.24 | Contactors
3.25 | Size 1 (27 Arms) | See Load List
3.26 | Size 2 (45 Arms) | See Load List
3.27 | Size 3 (90 Arms) | See Load List
3.28 | Size 4 (135 Arms) | See Load List
3.29 | Size 5 (270 Arms) | See Load List
3.3 | Size 6 (540 Arms) | See Load List
3.31 | Circuit Breakers
3.32 | 50A | See Load List
3.33 | 100A | See Load List
3.34 | 150A | See Load List
3.35 | 225A | See Load List
3.36 | 400A | See Load List
3.37 | Transformer and Panelboard
3.38 | Transformer Type | See Load List
3.39 | Transformer Voltage Rating | See Load List
3.4 | Transformer kVA Rating | See Load List
3.41 | Transformer Winding Material | See Load List
3.42 | Panelboard - Main Breaker | See Load List
3.43 | Panelboard - Number of Positions | See Load List
4 | Options
4.01 | Ground bus in each vertical wireway | Required
4.02 | Ground fault relays on all outgoing motor and breaker feeds | Not Required
4.03 | Vendor to reserve one vertical section for installation by Vendor of Purchaser furnished PLC or DCS I/O rack | Not Required
4.04 | Remote Racking | Not Required
5 | Spare Parts
5.01 | Power Fuses, Two (2) of Each Size, if applicable | Not Required
5.02 | Pilot Lights, Five (5) Spare of Each Color | Not Required
5.03 | Control Circuit Fuses, Two (2) Each of CPT Primary Fuses | Not Required
5.04 | Control Circuit Fuses, Two (2) Each of CPT Secondary Fuses | Not Required
5.05 | Two (2) spare contactors of each size used | Not Required
5.06 | Two (2) spare breakers or motor circuit protectors of each size | Not Required
5.07 | One (1) spare of each size starter | Required
5.08 | One Quart Touch Up Paint | Required
5.09 | Manufacturer Recommended Start-Up Spare Parts | Required
5.1 | Manufacturer Recommended Two-Year Spare Parts | Not Required
6 | Drawings Supplied as part of this Specification
6.01 | General Arrangement | Not Included
6.02 | Electrical One-Line | Included
6.03 | Equipment Layout | Included
6.04 | Typical Schematics | Not Included
7 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
7.01 | Outline/General Arrangement with overall dimensions, NTE weights, anchorage requirements | 6
7.02 | Electrical One-Line | 6
7.03 | Typical Schematics | 6
7.04 | Heat rejection data | 6
7.05 | Seismic Certification (if applicable) | 8 |  |  |  | Engineer to determine applicability
7.06 | O&M Manuals - Standard 3-ring binder | 4 weeks after delivery
7.07 | # of Proof copies required - 4 | N/A
7.08 | # of Final copies required - 8 | N/A
7.09 | # of CD's required - 8 | N/A
7.1 | Special O&M Manual requirements - None | N/A
8 | Additional Data to be supplied by Bidder
8.01 | Overall Dimensions (Length x Width x Height)
8.02 | Bill of Materials
8.03 | Shipping Weight (Lbs)
9 | Testing requirements
9.01 | Minimum number of factory acceptance tests Seller is expected to support | One
9.02 | Expected duration of each acceptance test | 2 Days
9.03 | Basic tests to include Seller is expected to support:
9.04 | Continuity test on all control cables with required documentation | Include
9.05 | Seller to apply voltage and function test all installed equipment | Include
9.06 | Point to Point wire checks including termination pull test to ensure cables are landed securely | Include
10 | Typical Payment Milestones
10.01 | If part of overall enclosure package, see enclosure specification
11 | Additional Data to be supplied by Bidder
11.01 | Overall Dimensions (Length x Width x Height)
11.02 | Bill of Materials
11.03 | Shipping Weight (Lbs)
12 | Additional Comments
12.01 | Motor starters shall be controlled by DCS (supplied by others) command (maintained) via Profibus simplex DP. Vendor to provide any interface devices that may be required to operate motor starters. Assume discrete 'start' and 'stop' signals will be coming from the DCS.
12.02 | Water treatment MCCs (WTT) will be shipped loose and housed in on site building construction.
12.03 | Provide indication of cable entry (bottom, top, or both) for 250HP 2 speed 1 winding starters (CTWR MCCs)
Note on C22: NEMA 1 Gasketed is typical for indoor MCCs. Choose this when no RFP requirements dictate otherwise. NEMA 2 Dripproof is Indoor rating with drip shield on top. NEMA 3R is Rainproof and Sleet Resistant - Outdoor, generally consists of a NEMA 1 indoor MCC mounted on a special base with an outdoor house erected around/over it. Non walk-in. NEMA 12 Dust-tight and Driptight - Indoor is gasketed all over, around doors, door cutouts, cover plates, side, top, and back sheets. This rating provides maximum protection against airborned particles and dripping liquids.
Note on B53: CBSchwartze: Motor Circuit Protector/Circuit Breaker (Mag only) is typical. Can replace with fused switch if required/desired.
Note on B54: CBSchwartze: typically withdrawable. Fixed is option. Large starters, NEMA 6 and up, may need to be fixed.
Note on B69: Should very rarely have any motors larger than 200hp and, if so, need to ensure that they can be started across-the-line before using a Size 6 starter
Note on B73: If there will be any 2-speed 1-winding motors then need to insert additional rows to cover those. These require 3 contactors to operate.
Note on B98: CBSchwartze: if applicable, add power panel requirements. It is useful to plan for a small panelboard internal to the MCC so that all of the motor space heater wiring can be factory installed and each motor space heater has a dedicated mcb in a panelboard integral to the MCC the motor is fed from.
Note on B104: CBSchwartze: Modify the number of circuits required if needed, if used only for motor space heaters, a 24 or 30 circuit panelboard would suffice.
Note on B108: Select Required if 480V system is solidly-grounded; select Not Required otherwise