## SPEC 84.03.08.200A - LVSG
Project: | [6 empty] | Notes
KED #:
Revision:
Date:
SPECIFICATION 831A/84.03.08.200A
LV Switchgear
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of low voltage metal-enclosed switchgear. All having the ratings and accessories as specified herein.
1 | Lineup General Requirements
1.01 | Lineup Name | See One Line
1.02 | Lineup Tag | See One Line
1.03 | Arrangement | Single Ended
1.04 | Installation Location | Indoors in Pre-Package Enclosure |  |  |  |  | Engineer to enter.
1.05 | Enclosure Rating | NEMA 1
1.06 | Color | Manufacturer's Standard
1.07 | Nominal Operating Voltage (V rms) | 480
1.08 | Maximum Rated Voltage (V rms) | 600
1.09 | Configuration | 3-Phase, 3-Wire
1.1 | System Grounding
1.11 | Type | High Resistance Grounded |  |  |  |  | High Resistance grounding is typical
1.12 | System Grounding Equipment Location | Integral with Switchgear
1.13 | Minimum Interrupting Current Capability (kA rms sym) | See One Line
1.14 | Arc-resistant Construction | Not Required |  |  |  |  | See RFP. If Arc-res is required, do not include fiber optic flash detection.
1.15 | Minimum Arcing Current Rating | Not Required
1.16 | Minimum Rated Arcing Duration
1.17 | Arc-flash Plenum | not required
1.18 | Main Bus
1.19 | Minimum Current Capability (A rms) | See One Line
1.2 | Material and Plating | Copper with Silver Plating
1.21 | Insulated Busbars | Required
1.22 | Neutral Bus (4-wire system only) | N/A
1.23 | Ground Bus, Full Length
1.24 | Material and Plating | Copper with Tin Plating
1.25 | Minimum Size | 1/4 x 2 inch
1.26 | Incoming Line Section
1.27 | Connection | Top Entry
1.28 | Conductor Type | Non-Seg Bus Duct
1.29 | Surge Arresters | N/A
1.3 | Outgoing Feeders
1.31 | Connection | Top and Bottom Entry
1.32 | Conductor Type | Cable
1.33 | Surge Arresters | N/A
1.34 | Control Cable Entry | Top and Bottom Entry
1.35 | Rear Doors | Lockable
1.36 | Front Doors | Lockable
1.37 | Compartment Space Heaters | Each Section
1.38 | Rated Voltage | 240VAC
1.39 | Energization Voltage | 120VAC
1.4 | Thermostats | One per Line Up
1.41 | Lights and Receptacles
1.42 | Lights, Fluorescent or LED, 120 VAC | Not Required
1.43 | Receptacles, Duplex 120 VAC | Not Required
1.44 | Power Source | External Provided by Others
2 | Control Power Requirements
2.01 | Trip | 125VDC
2.02 | Close | 125VDC
2.03 | Spring Charging Motor | 125VDC
2.04 | Protection Relays | 125VDC
3 | Metal-Clad Switchgear Requirements
3.01 | Standard(s) - Latest Revision | IEEE C37.13, C37.16, C37.17, C37.20.1
3.02 | Interrupter Insulating Medium | Air
3.03 | Removal | Horizontal Drawout
3.04 | Maximum Rated Interrupting Time (Cycles) | Manufacturer's Standard
3.05 | Maximum Rated Closing Time (Cycles) | Manufacturer's Standard
3.06 | Main Breaker Quantities
3.07 | Electrically-Operated | See One Line
3.08 | Tie Breaker Quantities
3.09 | Electrically-Operated | See One Line
3.1 | Feeder Breaker Quantities
3.11 | Electrically-Operated | See One Line
3.12 | Trip and Close Coil Monitoring | Required
3.13 | Auxiliary Contacts
3.14 | Spare Position Status Auxiliary Contacts | 2 'a' and 2 'b'
3.15 | Spare Stationary Position Status Contacts (aka MOC) - or Equal | 4 'a' and 4 'b'
3.16 | Spare Connection Status Contacts (aka TOC) | 2 N.O. and 2 N.C.
3.17 | Indicating Lights
3.18 | Open Status | Required - Green LED
3.19 | Closed Status | Required - Red LED
3.2 | Control Switch | Not Required
4 | Instrument Transformer Requirements
4.01 | Voltage Transformers
4.02 | Type | Withdrawable
4.03 | Accuracy Class | 0.3 WXY, 1.2Z
4.04 | Each Bus | 3-Phase Set Open-Delta Connected
4.05 | Incoming Side of Each Main | 1-Phase A-B Connected
4.06 | Current Transformers
4.07 | Relaying Accuracy Class | Not Required
4.08 | 3-Phase Set of CTs | Not Required
5 | Protection and Metering Requirements
5.01 | Solid State Trip Units | Included
5.02 | Microprocessor-based Tripping System with Current Sensors | Required
5.03 | Adjustable Phase Time Overcurrent Protection Functions | Required
5.04 | Adjustable Ground Time Overcurrent Fault Protection | Required
5.05 | Adjustable Maintenance Switch Function | Required
5.06 | Integral Metering and Display | Not Required
5.07 | Zone-Selective Interlocking Scheme | Not Required
5.08 | Datalink Interface | Required
5.09 | Main Sync-Check | SEL-751 |  |  |  |  | Basler BE1-25 is typical
5.1 | Fiber-Optic Arc Flash Detection System, Including CTs | SEL-751 |  |  |  |  | If Arc-res is required, do not include fiber optic flash detection.
5.11 | Differential Protection System, Including CTs | Not Required
5.12 | Maintenance Switch Scheme - Padlockable Switch and LED Armed Status Indicating Light | Required
5.13 | Metering
5.14 | Location(s) | Not Required
5.15 | Grade | N/A
5.16 | Manufacturer/Model Number | N/A
5.17 | Measured Quantities | N/A
5.18 | Datalink Requirements - Bidder to provide all equipment (media converters, protocol translation, multiplexing, etc.) to provide one external interface for communication datalink
5.19 | Protocol | Profibus
5.2 | Media | Profibus
6 | Wiring and Termination Requirements
6.01 | Wire Type | Type SIS
6.02 | Minimum Conductor Sizes for Internal Wiring
6.03 | Current Transformer Circuits | #10 AWG
6.04 | Voltage Transformer Circuits | #12 AWG
6.05 | Power | #12 AWG
6.06 | Instrumentation | #16 AWG
6.07 | Labeling | Cable Number and Opposite End
6.08 | Terminal Blocks
6.09 | Current Transformers | Shorting Type
6.1 | Voltage Transformers | Marathon or Equal
6.11 | Power (Low Voltage) | Marathon or Equal
6.12 | Control | Marathon or Equal
6.13 | Terminal Lugs
6.14 | Current Transformer Circuits | Ring Tongue
6.15 | Voltage Transformer Circuits | Ring Tongue
6.16 | Auxiliary Power | Ring Tongue
6.17 | Control | Ring Tongue
7 | Additional Items and Spare Parts
7.01 | Test Cabinet for Operating Breaker Outside Compartment | Required
7.02 | Lift Truck | Required
7.03 | Mimic Bus | Not Required
7.04 | Remote Racking System | Yes - Portable
7.05 | IR Inspection Ports | Not Required
7.06 | Spare Parts
7.07 | Five (5) Spare LEDs of Each Color | Required
7.08 | Control Circuit Fuses, 50% Spare | Required
7.09 | One Set of Spare VT Primary Fuses (2 Total) | Required
7.1 | One Set of Spare VT Secondary Fuses | Required
7.11 | One Quart Touch Up Paint | Required
7.12 | Manufacturer Recommended Start-Up Spare Parts | Required
7.13 | Manufacturer Recommended Two-Year Spare Parts | Not Required
8 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
8.01 | Outline/General Arrangement with overall dimensions, NTE weights, anchorage requirements | 6
8.02 | Electrical One-Line and Three-Line Diagram | 6
8.03 | Typical Schematics including terminal numbers | 6
8.04 | Heat rejection data | 6
8.05 | Seismic Certification (if applicable) | 8 |  |  |  | Engineer to determine applicability
8.06 | O&M Manuals - Standard 3-ring binder | 4 weeks after delivery
8.07 | # of Proof copies required - 4 | N/A
8.08 | # of Final copies required - 8 | N/A
8.09 | # of CD's required - 8 | N/A
8.1 | Special O&M Manual requirements - None | N/A
9 | Testing requirements
9.01 | Minimum number of factory acceptance tests Seller is expected to support | One
9.02 | Expected duration of each acceptance test | 2 Days
9.03 | Basic tests to include Seller is expected to support:
9.04 | Continuity test on all control cables with required documentation | Include
9.05 | Seller to apply voltage and function test all installed equipment including multi-function relays, lock out relays, test switches, racking mechanisms, lights, breakers, etc. | Include
9.06 | Point to Point wire checks including termination pull test to ensure cables are landed securely | Include
10 | Typical Payment Milestones
10.01 | If part of overall enclosure package, see enclosure specification
11 | Drawings Supplied as part of this Specification
11.01 | General Arrangement | Not Included
11.02 | Electrical One-Line | Included
11.03 | Equipment Layout | Included
11.04 | Typical Schematics | Not Included
12 | Additional Data to be supplied by Bidder
12.01 | Manufacturer
12.02 | Manufacturing Location
12.03 | Overall Dimensions (Length x Width x Height)
12.04 | Total Weight (lbs)
12.05 | Shipping Weight (lbs)
13 | Additional Requirements
13.01
13.02
13.03
13.04
13.05
13.06