## 94.03.08.175B 94.03.08.125.02
Project: | HICKORY RUN ENERGY CENTER | [5 empty] | Notes
KED #:
Revision: | A
Date: | 42663
SPECIFICATION 830B/821A/94.03.08.175B/94.03.08.125.02
Medium Voltage Metal-Clad Switchgear and/or Motor Control Assemblies
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing, and delivery of medium-voltage metal-clad switchgear, medium-voltage motor controllers, or integrated assembly with both medium-voltage metal-clad switchgear and medium-voltage motor controllers. All having the ratings and accessories as specified herein.
1 | Lineup General Requirements
1.01 | Lineup Name | MV SWITCHGEAR
1.02 | Lineup Tag | 1Z-MVC-SWG-01/1Z-MVC-SWG-02
1.03 | Installation Location | Indoors in Pre-Package Enclosure |  |  |  |  | Engineer to enter.
1.04 | Enclosure Rating | NEMA 1
1.05 | Nominal Voltage Class (kV) | 6.9
1.06 | Configuration | 3-Phase, 3-Wire
1.07 | System Grounding
1.08 | Type | Low Resistance Grounded |  |  |  |  | Low Resistance grounding is typical
1.09 | Current | 400 Amps
1.1 | Grounding Equipment Location | External Provided by Others
1.11 | Minimum Interrupting Current Capability (kA rms sym.) (K=1) | 50
1.12 | Arc-resistant Construction | Not Required |  |  |  |  | See RFP. If Arc-res is required, do not include fiber optic flash detection.
1.13 | Minimum Arcing Current Rating | Not Required
1.14 | Minimum Rated Arcing Duration
1.15 | Arc-flash Plenum | Not Required
1.16 | Configuration | Two High
1.17 | Main Bus
1.18 | Minimum Current Capability (A rms) | 4000 A
1.19 | Material and Plating | Copper with Silver Plating
1.2 | Insulated Busbars | Required
1.21 | Neutral Bus | Neutral Bus Not Required
1.22 | Ground Bus, Full Length
1.23 | Material and Plating | Copper with Tin Plating
1.24 | Minimum Size | 1/4 x 2 inch
1.25 | Incoming Line Section
1.26 | Connection | Top Entry
1.27 | Conductor Type | Non-Seg Bus Duct
1.28 | Surge Arresters | Yes - 1 per Phase
1.29 | Outgoing Feeders
1.3 | Connection | Bottom Entry
1.31 | Conductor Type | Cable
1.32 | Surge Arresters | N/A
1.33 | Control Cable Entry | Top and Bottom Entry
1.34 | Rear Doors | Lockable
1.35 | Front Doors | Lockable
1.36 | Compartment Space Heaters | Each Section
1.37 | Rated Voltage | 240VAC
1.38 | Energization Voltage | 120VAC
1.39 | Thermostats | One per Line Up
1.4 | Lights and Receptacles
1.41 | Lights, Fluorescent or LED, 120 VAC | Not Required
1.42 | Receptacles, Duplex 120 VAC | Not Required
1.43 | Power Source | External Provided by Others
1.44 | Terminal Blocks
1.45 | Current Transformers | Shorting Type
1.46 | Voltage Transformers | Marathon or Equal
1.47 | Power (Low Voltage) | Marathon or Equal
1.48 | Control | Marathon or Equal
2 | Control Power Requirements
2.01 | Switchgear Breakers
2.02 | Trip | 125VDC
2.03 | Close | 125VDC
2.04 | Spring Charging Motor | 125VDC
2.05 | Protection Relays | 125VDC
2.06 | Contactors
2.07 | Coil | Internal 120VAC CPT
2.08 | Protection Relays | 125VDC
2.09 | Disconnect Switch | Not Applicable
3 | Metal-Clad Switchgear Requirements
3.01 | Standard - Latest Revisions | IEEE C37.20.2, IEEE C37.06
3.02 | Interrupter Insulating Medium | Vacuum
3.03 | Removal | Horizontal Drawout
3.04 | Arrangement | Two Breakers per Vertical Section
3.05 | Maximum Rated Interrupting Time (Cycles) | Manufacturer's Standard
3.06 | Maximum Rated Closing Time (Cycles) | Manufacturer's Standard
3.07 | Feeder Breaker Quantities
3.08 | 1200A | 14
3.09 | 2000A | 0
3.1 | 3000A | 0
3.11 | 4000A | 0
3.12 | Quantity of Trip Coils per Each Breaker | One
3.13 | Trip Coil Monitoring | Required
3.14 | Auxiliary Contacts
3.15 | Spare Position Status Auxiliary Contacts | 2 'a' and 2 'b'
3.16 | Spare Stationary Position Status Contacts (aka MOC) | 4 'a' and 4 'b'
3.17 | Spare Connection Status Contacts (aka TOC) | 2 N.O. and 2 N.C.
3.18 | Indicating Lights
3.19 | Open Status | Required - Green LED
3.2 | Closed Status | Required - Red LED
3.21 | Control Switch | Required - Control in Test Position Only
4 | Medium-Voltage Disconnect Switch Requirements
4.01 | Standard - Latest Revision | N/A
4.02 | Switch Type | N/A
4.03 | Operator | N/A
4.04 | Mechanical Interlocks with Compartment Door | N/A
4.05 | Quantity and Continuous Current Rating | N/A
4.06 | Fuses | N/A
4.07 | Spare Position Status Auxiliary Contacts | N/A
4.08 | Indicating Lights
4.09 | Open Status | N/A
4.1 | Closed Status | N/A
4.11 | Control Switch | N/A
5 | Medium Voltage Motor Control Center Requirements | [5 empty] | Limitations for an MV MCC is 3000A bus and 50kA. If a 4000A SWGR is required, move to all SWGR breakers
5.01 | Standard - Latest Revision | NEMA ICS3
5.02 | Interrupter Insulating Medium | Vacuum
5.03 | NEMA E2 Fused FVNR Motor Controller Quantities
5.04 | 400A Drawout | 5
5.05 | 800A Drawout | 0
5.06 | NEMA E2 Fused 2-Speed FVNR Motor Controller Quantities
5.07 | 400A Drawout | N/A
5.08 | Fused Mechanically-Latched Contactor Quantities
5.09 | 400A Drawout | N/A
5.1 | 800A Drawout | N/A
5.11 | Auxiliary Contacts
5.12 | Spare Position Status Auxiliary Contacts | 2 'a' and 2 'b'
5.13 | Spare Mechanism-Operated Contacts (MOC) | 4 'a' and 4 'b'
5.14 | Spare Truck-Operated Contacts (TOC) | 2 N.O. and 2 N.C.
5.15 | Indicating Lights
5.16 | Open Status | Required - Green LED
5.17 | Closed Status | Required - Red LED
5.18 | Test Pushbutton | Required - Control in Test Position Only
5.19 | Emergency Stop Pushbutton | Manufacturer's Standard
6 | Instrument Transformer Requirements
6.01 | CT Relaying Accuracy Class | Best Possible for Each Application
6.02 | Voltage Transformers
6.03 | Type | Withdrawable
6.04 | Accuracy Class | 0.3 WXY, 1.2Z
6.05 | Each Bus | 3-Phase Set Wye-Wye Connected
6.06 | Incoming Side of Each Main | 1-Phase B-N Connected
6.07 | Current Transformers
6.08 | Relaying Accuracy Class | Best Possible for Available Space
6.09 | 3-Phase Set of CTs | As Required
6.1 | Zero-Sequence CTs
6.11 | Location(s) | Each Feeder
6.12 | Ratio | 50:5
7 | Relay and Metering Requirements
7.01 | Main/Tie Protection | SEL-751
7.02 | Voltage Input | Required
7.03 | Sync-check Function | Required
7.04 | Undervoltage Function | Required
7.05 | UAT Transformer Protection | SEL-787
7.06 | Voltage Input | Required
7.07 | Overexcitation Protection Function | Required
7.08 | Lockout Relay associated with 787 | Required
7.09 | Motor Feeder Protection | SEL-710
7.1 | Voltage Input | Required
7.11 | Winding RTD Temperature Input | Required - 6 RTDs
7.12 | Bearing RTD Temperature Input | Required - 2 RTDs
7.13 | Ambient RTD Temperature Input | Required
7.14 | Non-Motor Feeder Protection | SEL-751A
7.15 | Voltage Input | Required
7.16 | Lockout Relays
7.17 | Location(s) | Main Breakers only
7.18 | Manufacturer/Model | Electroswitch Series 24
7.19 | Integral Indicating Lights (LED) | Coil Monitoring and Lockout Tripped
7.2 | Separate Indicating Lights (LED) | Not Required
7.21 | IEC 61850 Communication Required with Each Relay | Not Required
7.22 | Arc-Flash Fiber Optic Detection Scheme | Required |  |  |  |  | If Arc-res is required, do not include fiber optic flash detection.
7.23 | Differential Protection Scheme, Including CTs | Not Required |  |  |  |  | Not typical. Only for motors over 3000 HP.
7.24 | Zone-Selective Interlocking Scheme | Not Required |  |  |  |  | Not typical.
7.25 | Maintenance Switch Scheme for Lineup, including Arming Light and Padlockable Switch | Required
7.26 | GPS Clock | Not Required
7.27 | IRIG-B Signal Distribution | Required
7.28 | Metering
7.29 | Location(s) | Not Required
7.3 | Grade | N/A
7.31 | Manufacturer/Model Number | N/A
7.32 | Measured Quantities | N/A
7.33 | Datalink Requirements - Bidder to provide all equipment (media converters, protocol translation, multiplexing, etc.) to provide one external interface for communication datalink
7.34 | Protocol | Modbus
7.35 | Media | Cat6
7.36 | Ethernet Switch | required
7.37 | CAT 6 wiring from ethernet switch to relays | required
8 | Wiring and Termination Requirements
8.01 | Wire Type | Type SIS
8.02 | Minimum Conductor Sizes for Internal Wiring
8.03 | Current Transformer Circuits | #10 AWG
8.04 | Voltage Transformer Circuits | #12 AWG
8.05 | Power | #12 AWG
8.06 | Control | # 14 AWG
8.07 | Labeling | Opposite End and Ckt name
8.08 | Terminal Lugs
8.09 | Current Transformer Circuits | Ring Tongue
8.1 | Voltage Transformer Circuits | Ring Tongue
8.11 | Power (Low Voltage) | Ring Tongue
8.12 | Control | Ring Tongue
9 | Additional Items and Spare Parts
9.01 | Test Cabinet for Operating Breaker Outside Compartment | Required
9.02 | Lift Truck | Required
9.03 | Mimic Bus | Not Required
9.04 | Remote Racking System | Yes - Portable
9.05 | IR Inspection Ports | Not Required
9.06 | Grounding and Test Device(s) | Yes
9.07 | Spare Parts
9.08 | Power Fuses, Two (2) of Each Size | Not Required
9.09 | Five (5) Spare LEDs of Each Color | Not Required
9.1 | Control Circuit Fuses, 50% Spare | Not Required
9.11 | One Set of Spare VT Primary Fuses (2 Total) | Not Required
9.12 | One Set of Spare VT Secondary Fuses | Not Required
9.13 | One Quart Touch Up Paint | Required
9.14 | Manufacturer Recommended Start-Up Spare Parts | Required
9.15 | Manufacturer Recommended Two-Year Spare Parts | Not Required
10 | Drawings Supplied as part of this Specification
10.01 | General Arrangement | Not Included
10.02 | Electrical One-Line | Included
10.03 | Equipment Layout | Included
10.04 | Typical Schematics | Not Included
11 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
11.01 | Outline/General Arrangement with overall dimensions, NTE weights, anchorage requirements | 6
11.02 | Electrical One-Line and Three-Line Diagram | 6
11.03 | Typical Schematics including terminal numbers | 6
11.04 | Heat rejection data | 6
11.05 | Seismic Certification (if applicable) | 8 |  |  |  | Engineer to determine applicability
11.06 | O&M Manuals - Standard 3-ring binder (follow enclosure contract schedule if purchased under the same contract) | 4 weeks after delivery
11.07 | # of Proof copies required - 4 | N/A
11.08 | # of Final copies required - 8 | N/A
11.09 | # of CD's required - 8 | N/A
11.1 | Special O&M Manual requirements - None | N/A
12 | Testing requirements
12.01 | Minimum number of factory acceptance tests Seller is expected to support | One per every two MV lineups
12.02 | Expected duration of each acceptance test | 5 Days
12.03 | Basic tests to include Seller is expected to support:
12.04 | Continuity test on all control cables with required documentation | Include
12.05 | Seller to apply voltage and function test all installed equipment including multi-function relays, lock out relays, test switches, racking mechanisms, lights, breakers, etc. | Include
12.06 | Point to Point wire checks including termination pull test to ensure cables are landed securely | Include
12.07 | Voltage transformer ratio tests | Include
12.07 | Current transformer ratio tests | Include
12.08 | Maintenance switch functionality testing (if applicable) | Include
13 | Typical Payment Milestones
13.01 | If part of overall enclosure package, see enclosure specification
14 | Additional Data to be supplied by Bidder
14.01 | Metal-Clad Switchgear
14.02 | Manufacturer
14.03 | Location
14.04 | Medium-Voltage Motor Control Center
14.05 | Manufacturer
14.06 | Location
14.07 | Medium-Voltage Disconnect Switches
14.08 | Manufacturer
14.09 | Location
14.1 | Overall Dimensions (Length x Width x Height) (inches)
14.11 | Total Weight (lbs)
14.12 | Shipping Weight (lbs)
14.13 | Channel Sills Required (if so, Bidder to Provide)
15 | Additional Requirements
15.01
15.02