## SPEC 835 - GCB
Project: | [5 empty] | Notes
KED #:
Revision:
Date:
SPECIFICATION 94.03.12.200
Generator Circuit Breaker(s)
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of Generator Circuit Breaker(s) in accordance with this specification and stated Standards. Site parameters can be found in additional attachments.
1 | General Requirements
1.01 | Description | IPBD Connected to CTG |  |  |  | Engineer to enter.
1.02 | Quantity | One (1) Unit
1.03 | Rated Operating Voltage (kV) | 23.5 nominal (25 max)
1.04 | BIL (kV) | 150 |  |  |  | 110 for 17kV maximum voltage; 150 for 26kV max voltage; 200 for 36kV max voltage
1.05 | Minimum Rated Continuous Current @ 20°C (A) | 16000 |  |  |  | See ETAP or OEM generator information.
1.06 | Minimum Rated Continuous Current @ 40°C (A) | 14000 |  |  |  | See ETAP or OEM generator information.
1.07 | Rated Short Circuit Current Interrupting Capacity (kA) | 200 symm. 3 phase |  |  |  | See ETAP or OEM generator information.
1.08 | Frequency (HZ) | 60
2 | Control Cabinet
2.01 | Cabinet for Each Breaker | Included
2.02 | Gasketed, Weatherproof Outdoor Design | Included
2.03 | Heaters rated for 240VAC | Included
2.04 | Trip coil monitoring relay | Included
3 | Support Structure
3.01 | Self Supporting, Elevated, Galvanized Steel Structure | Included, Vendor to provide # of tons of steel |  |  |  | Verify support steel is not carried by structural or ISBD vendor.
3.02 | Centerline Height of Breaker Above Foundation | 31'
3.03 | Skid Mounted Assembly | Included
3.04 | Maintenance Platform and Access Ladder | Included
4 | Additional Items
4.01 | Isolation Switches | Included
4.02 | Three-Pole Motor Operated No Load Switch Located on the Transformer Side and in Series with Each Interrupter
4.03 | Visual Verification inspection windows for all three phases showing each isolation switch position | Included
4.04 | Grounding Switches | Included
4.05 | Three-Pole Motor Operated No Load Switch Provided on Both Sides of the Breaker
4.06 | Surge Arrestors and Capacitors | Included
4.07 | Located on the Transformer Side Ahead of the Isolation Switches
4.08 | Current Transformers
4.09 | Number of 3-Phase Sets | Four (4)
4.1 | Location to be Installed | Transformer and Generator Sides
4.11 | Ratio | 16000:5
4.12 | Relay Accuracy Class | C-800
4.13 | Voltage Transformers
4.13 | Number of Dual Secondary Sets | One (1) |  |  |  | 1 is typical
4.14 | Number of 2-winding Sets | Two (2) |  |  |  | Only required for GE single shaft estimates
4.15 | Secondary Line-to-Line Voltage | 120 VAC
4.16 | Accuracy Class | 0.3
4.17 | Breaker Operating Mechanism | Spring
4.18 | Internal Insulation (Vendor to provide SF6 gas fill) | SF6 gas
4.19 | Starting Switch |  |  |  |  | See 89SS Guideline document for details on switch.
4.19 | Quantity | One (1) |  |  |  | Only required for GE single shaft estimates
4.2 | Rated Maximum voltage | 25kV |  |  |  | Only required for GE single shaft estimates
4.21 | Minimum Rated Continuous current | 2000A |  |  |  | Only required for GE single shaft estimates
4.22 | Rated Short Time Current Carrying Capability at 1 sec (kA) | 63kA |  |  |  | Only required for GE single shaft estimates. Match MV SWGR rating
4.23 | Power and Control Voltage | 120VAC |  |  |  | Only required for GE single shaft estimates
5.19 | Power Supplies (Provided by others)
4.24 | Auxiliary Power | 480V 3-Phase
4.25 | Control DC | 125V
5 | Spare Parts
5.01 | Manufacturer Recommended Start-Up Spare Parts | Required
5.02 | Manufacturer Recommended Two-Year Spare Parts | Not Required
6 | Codes and Standards
6.01 | Follow All the Latest Applicable Standards and Codes Including but Not Limited To
6.02 | American Institute of Steel Contruction (AISC)
6.03 | American National Standards Institute (ANSI)
6.04 | American Society of Testing and Materials (ASTM)
6.05 | Canadian Electrical Code (CEC) | N/A
6.06 | Canadian Standards Association (CSA) | N/A
6.07 | Institute of Electrical and Electronic Engineers (IEEE)
6.08 | IEEE C37.06
6.09 | IEEE C37.09
6.1 | IEEE C37.013
6.11 | IEEE C57.13
6.12 | IEEE C57.13.2
6.13 | IEEE C62.11
6.13 | National Electric Code (NEC)
6.14 | National Electric Safety Code (NESC)
6.15 | National Electrical Manufacturers Association (NEMA)
6.16 | NEMA ICS-1
6.17 | NEMA ICS-2
6.18 | National Fire Protection Association (NFPA)
6.19 | Underwriters Laboratories (UL)
6.2 | Other
7 | Drawings Supplied as part of this Specification
7.01 | One Line Schematic of Generator Circuit Breakers | Included
7.02 | GE Specification for motor operated Static Start Switch (89SS) | Included
8 | Data to be supplied by Vendor
8.01 | Rated Continuous Current @ 20°C (A)
8.02 | Rated Continuous Current @ 40°C (A)
8.03 | Rated Breaker Sym. Current Interrupting Capability (kA, rms)
8.04 | Maximum Rated Operating Voltage (kV)
8.05 | Rated Breaker BIL (kV)
8.06 | Structural Steel, Weight in Pounds (lbs)
8.07 | ISBD termination Center to center spacing (in)
9 | Additional Comments
9.01