## 94.03.20.100
Project: | [5 empty] | Notes | TJE Comments
KED #:
Revision:
Date:
SPECIFICATION 800A/94.03.20.100
Generator Step Up Transformer
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of Generator Step Up Transformer(s) in accordance with this specification and stated Standards.
1 | General Requirements
1.01 | Quantity | One (1) |  |  |  | Engineer to enter.
1.02 | Tag Number | See One Line
1.03 | Cooling Class | ONAN/ONAF/ONAF |  |  |  | ONAN/ONAF/ONAF typical
1.04 | Temperature Rise | 65°C |  |  |  | 65°C typical | Add reference in case 55 C rating is needed?
1.05 | Number of Windings | 2 |  |  |  | Engineer to enter.
1.06 | Frequency (Hz) | 60
1.07 | Near Field Sound Pressure Level (dbA) at 3 Feet | 85 |  |  |  | Engineer to verify no special RFP requirements
1.08 | Impedance at Base Rating (%) | 9% |  |  |  | Engineer to enter. Verify RFP has no special requirements for Grid impedance limitations
1.09 | Evaluation Basis for losses ( $ / kW ) | 1500 |  |  |  | Engineer to enter.
1.1 | Efficiency at Top MVA Rating | 99.7% |  |  |  | 99.7% typical GSU value
2 | Windings Requirements
2.01 | Winding # 1, HV
2.02 | Rated Power per cooling class (MVA) | 330/439/550 |  |  |  | (A = generator max MVA*.6) / (A*1.33) / (Generator max MVA) | Think about revising to reference heat balances and margins
2.03 | Rated Voltage (kV) | 230 |  |  |  | Engineer to enter. See RFP
2.04 | Connection | Wye |  |  |  | Wye typical
2.05 | Line BIL (kV) | 900 |  |  |  | See Useful information tab
2.06 | Neutral BIL (kV) | 150 |  |  |  |  | Neutral BIL not on useful info tab. Can we add?
2.07 | Winding # 2, XV
2.08 | Rated Power (MVA) | 330/439/550
2.09 | Rated Voltage (kV) | 23.5 |  |  |  |  | Engineer to enter
2.1 | Connection | Delta |  |  |  | Delta typical
2.11 | Line BIL (kV) | 150 |  |  |  | See Useful information tab
2.12 | Neutral BIL (kV) | NA
2.13 | Buried Delta Winding | NA
2.14 | Vector Group | Low lags high by 30 deg
2.15 | Winding Material | 100% copper |  |  |  | Copper typical
2.16 | Maximum Winding Hot Spot Rise Above Ambient (°C) | 80 |  |  |  | Engineer to enter. 80 typical
3 | Insulating Material
3.01 | Type of Insulating Material - Seller to furnish all required insulating material | Mineral Oil |  |  |  | Mineral Oil typical
3.02 | Insulating Material Preservation | conservator |  |  |  | Engineer to enter. See RFP | Conservator typical for GSU
4 | Tap Changers
4.01 | Regulated Winding | HV Winding |  |  |  | HV Winding typical
4.02 | Tap Changer Type | Off-Load |  |  |  | Off-Load typical
4.03 | Tap Changer Control | Manual Hand Crank |  |  |  | Manual Hand Crank typical
4.04 | Number of Steps Plus - Increment | 2 @ 2.5% |  |  |  | 2 @ 2.5% typical
4.05 | Number of Steps Minus - Increment | 2@2.5% |  |  |  | 2@2.5% typical
5 | Bushings
5.01 | High Voltage, HV Rated Line Voltage (kV) | 230
5.02 | Bushing Material | Porcelain |  |  |  | Porcelain typical
5.03 | BIL (kV) | 900 |  |  |  |  | Useful information tab? Refer to correct table if so
5.04 | Minimum Porcelain Creep Distance (Inches) | 28mm/kV |  |  |  | Between 28 and 44mm/kV | Useful information tab. Manufacturer's standard when no EPC requirements called out?
5.05 | Termination Compartment | No
5.06 | Termination Type | Cable |  |  |  | HV cable is typical
5.07 | HO Neutral Bushing BIL (kV) | 150
5.08 | Low Voltage, XV Rated Line Voltage (kV) | 23.5
5.09 | Bushing Material | Porcelain
5.1 | BIL (kV) | 150
5.11 | Minimum Porcelain Creep Distance (Inches) | Manufacturer Standard
5.12 | Termination Compartment | Yes
5.13 | Termination Type | Isolated Phase Bus Duct
5.14 | XO Neutral Bushing BIL (kV) | NA
6 | Neutral Grounding Equipment
6.01 | Connection Point | High Voltage Winding |  |  |  | High Voltage Winding typical
6.02 | Method | Solid |  |  |  | Solid typical
6.03 | Rated Voltage (kV) | NA |  |  |  | Phase to ground voltage
6.04 | Resistor | No
6.05 | Amperes | NA |  |  |  | Typically 400A for Low Resistance, and 5A for High Resistance Grounding systems. Typical is Low Res for GSU | The low resistance is for UATs. Suggest deleting this comment to avoid confusion.
6.06 | Ohms | NA
6.07 | Time Duration (Seconds) | NA |  |  |  | Typical duration for low resistance grounded systems is 10 seconds. For high resistance grounded systems duration is usually continuous. | Suggest deleting this comment to avoid confusion.
6.08 | Mounted on Transformer | NA
7 | Additional Items (See RFP for additional Accessories)
7.01 | Surge Arresters
7.02 | Quantity | 3 |  |  |  | Engineer to enter. 3 is typical if required
7.03 | Minimum MCOV Rating (kV) | 190 |  |  |  | See Useful information tab if required | Table reference?
7.04 | Mounted on Transformer | Yes |  |  |  | If required, Yes is typical
7.05 | Discharge Counters | No |  |  |  | No is typical
7.06 | Current Transformers
7.07 | HV Bushing | Included
7.08 | Ratio | 2000:5 MR |  |  |  |  | Engineer to calculate based on top transformer MVA.
7.09 | Relay Accuracy Class / Quantity per bushing / total | C-800 / 3 per bushing / 9 total |  |  |  |  | Three is typical. Verify with relaying sketch. Ensure there are no metering requirements in RFP.
7.1 | Meter Accuracy Class / Quantity per bushing / total | NA
7.11 | HO Bushing | Included
7.12 | Ratio | 2000:5 MR |  |  |  |  | Engineer to calculate based on top transformer MVA.
7.13 | Relay Accuracy Class / Quantity per bushing / total | C-800 / 1 per bushing / 1 total |  |  |  |  | Typical
7.14 | XV Bushing | Included
7.15 | Ratio | 16000:5 MR |  |  |  |  | Engineer to calculate based on top transformer MVA.
7.16 | Relay Accuracy Class / Quantity per bushing / total | C-800 / 3 per bushing / 9 total |  |  |  |  | Three is typical. Verify with relaying sketch. Ensure there are no metering requirements in RFP.
7.17 | Protection Devices
7.18 | Winding Temperature Indicator | Included
7.19 | Oil Temperature Indicator | Included
7.2 | Oil Level Gauge | Included
7.21 | Pressure Gauge and Relief Valve | Included
7.22 | Sudden Pressure Relay | Included
7.23 | Buchholz Relay | Included |  |  |  | Typical for GSU | Typical for conservator type transformer
7.24 | Gas Monitor (GE Hydran or equal) | Included |  |  |  | GE Hydran Monitor M2 to be included for Single Shaft estimates
7.25 | Technical Service
7.26 | Three (3) days Technical Supervision at first filling | Included
7.27 | Three (3) days Technical Supervision at Power up | Included
7.28 | Power Supplies (Provided by others)
7.29 | Auxiliary Power | 480V 3-Phase - Qty 2 with automatic transfer switch provided by Supplier
7.3 | Control DC | 125V with loss of DC alarm
7.31 | Paint System and Color
7.32 | Tank and Accessories Color | ANSI 70 Light Gray
7.33 | Painting System | Manufacturer Standard
7.34 | Porcelain Color | Gray
8 | Spare Parts
8.01 | HV Bushing | N/A
8.02 | LV Bushing | N/A
8.03 | Neutral Bushing | N/A
8.04 | Full Set of Gaskets | Included
8.05 | Enclosure for Noise Level Reduction | N/A
8.06 | Winding Temperature Indicator | N/A
8.07 | Manufacturer Recommended Start-Up Spare Parts | Included
8.08 | Manufacturer Recommended Two-Year Spare Parts | N/A
9 | Required Testing
9.01 | Minimum number of witnessed factory tests per order | One - Seller to inform if the possibility of performing all tests in one trip would not be possible
9.02 | Expected duration of each acceptance test | 5 Days
9.03 | Manufacturer's Standard Testing | Included
9.04 | ANSI C57.12.00 and C57.12.90 Factory Test Requirements:
9.05 | Resistance Measurement Test | Included
9.06 | Polarity and Phase Relation Tests | Included
9.07 | Ratio Tests | Included
9.08 | No-Load and Excitation Current Tests | Included
9.09 | Load Losses and Impedance Voltage Tests | Included
9.1 | Excitation current at rated voltage and frequency on the rated voltage connection and at the extremes | Included
9.11 | Impedance volts and load loss at rated current and frequency at nominal and extreme taps | Included
9.12 | Zero phase sequence test | Included
9.13 | Impulse test | Included
9.14 | Temperature rise test | Included
9.15 | Bushing power factor testing if not included as part of the bushing manufacturer's certified test report | Included
9.16 | Dew point tests at the factory prior to shipment. | Included
9.17 | Sweep frequency response analysis test using Doble M5x00 at the factory when fully assembled and filled with oil | Included
9.18 | Sweep frequency response analysis test using Doble M5x00 using spark plug bushings when the unit is ready for shipping without oil or bushings | Included
9.19
9.2 | Field testing (applicable when assembly, oil fill, and testing is in supplier scope) |  |  |  |  | Include only if dress out, oil fill, and testing is in vendor scope
9.21 | Dew point tests when the transformer arrives on site and after complete installation | Included
9.21 | Sweep frequency response analysis test using Doble M5x00 using spark plug bushings when the transformer arrives at site and is set on the final pad | Included
9.22 | Sweep frequency response analysis test using Doble M5x00 using spark plug bushings when the transformer is assembled with normal in service bushing and filled with oil | Included
9.23 | Insulation tests on all auxiliary devices and wiring (megger) | Included
9.24 | Transformer turns ratio | Included
9.25 | Power factor - 10kV or LV Cap Bridge | Included
9.26 | Core Megger | Included
9.27 | Insulation resistance | Included
9.28 | CT Ratio, polarity, and saturation | Included
9.29 | On-load tap changer operation (if required) | Included
9.3 | LTC and motor drive operation (if required) | Included
9.31 | Check operation of alarm, interlock, trip circuits, and all ancillary equipment including bushing monitor, gas monitor, etc. | Included
9.32 | Detailed test reports required | Included
10 | Codes and Standards
10.01 | Follow All the Latest Applicable Standards and Codes Including but Not Limited To
10.02 | American National Standards Institute (ANSI)
10.03 | American Society of Testing and Materials (ASTM)
10.04 | ASTM D3487-88
10.05 | Canadian Electrical Code (CEC) | N/A
10.06 | Canadian Standards Association (CSA) | N/A
10.07 | Institute of Electrical and Electronic Engineers (IEEE)
10.08 | IEEE C37.23
10.09 | IEEE C57.12.00
10.1 | IEEE C57.12.10
10.11 | IEEE C57.12.70
10.12 | IEEE C57.12.90
10.13 | IEEE C57.13
10.14 | IEEE C57.13.2
10.15 | IEEE C57.19.00
10.16 | IEEE C57.19.01
10.17 | IEEE C57.91
10.18 | IEEE C57.016
10.19 | IEEE C57.109
10.2 | IEEE C57.116
10.21 | IEEE C57.121
10.22 | IEEE C62.11
10.23 | National Electric Code (NEC)
10.24 | National Electric Safety Code (NESC)
10.25 | National Electrical Manufacturers Association (NEMA)
10.26 | NEMA ICS1
10.27 | NEMA ICS2
10.28 | National Fire Protection Association (NFPA)
10.29 | Underwriters Laboratories (UL)
10.3 | Other
11 | Required Production Documentation (not limited to the list below) | Weeks after NTP (unless noted otherwise)
11.01 | O&M Manuals - Standard 3-ring binder | 4 weeks after delivery
11.02 | # of Proof copies required - 4 | N/A
11.03 | # of Final copies required - 8 | N/A
11.04 | # of CD's required - 8 | N/A
11.05 | Special O&M Manual requirements - None | N/A
11.06 | Outline/General arrangement showing the following: - Not to exceed loads and dimensions to begin foundation design - Locations of major equipment - Not to exceed oil volume - Dimensional data for bushing, lightning arresters, bus duct connections, tank and conservator, radiator, guages, and other accessories - HV and LV connection details - Estimated center of gravity - Shipping and assembled weights and dimensions, oil quantities, and bill of materials | 6
11.07 | Outline/General Arrangement Drawing Containing the Following Information as a Minimum: - Final overall dimensions - Final oil volume | 10
11.08 | Electrical drawings needed to complete power and control interface wiring | 6
11.09 | Design data and transformer performance curves including: - Overexcitation capability - MVA capability vs. average ambient temperature - I2t damage curves - Short circuit capability calculations | 6
11.1 | Transformer nameplate drawing | 6
12 | Typical Payment Milestones
12.01 | Upon proof of purchase by redacted purchase order of long lead material | 5%
12.02 | Upon submittal of approved or approved as noted engineering deliverables | 10%
12.03 | Upon proof of completion of the core and coil assembly (pictures or signed inspection/test documents) | 25%
12.04 | Upon proof of completion of successful witnessed factory acceptance tests | 10%
12.05 | Upon complete delivery and acceptance of transformers and loose shipped equipment to project site | 45%
12.06 | Upon Contractor approval of final O&M manuals and all outstanding engineering deliverables | 5%
13 | Expected Delivery | 12 months after NTP |  |  |  | Based on project schedule
14 | Data to be supplied by Manufacturer
14.01 | Guaranteed Losses
14.02 | No Load Losses (kW) at Unity Power Factor
14.03 | Load Losses at Base MVA (kW) at Unity Power Factor
14.04 | Total Losses at Base MVA (kW) at Unity Power Factor
14.05 | Impedance at Base MVA (%)
14.06 | X/R Ratio
14.07 | Zero Phase Sequence Impedance (%)
15 | Other Information
15.01 | Overall Dimensions (Length x Width x Height) | By Vendor
15.02 | Shipping Weight (Lbs) | By Vendor
15.03 | Total Installed Weight including Oil (Lbs) | By Vendor
15.04 | Total Insulating Liquid quantity (US Gal) | By Vendor
15.05 | Shipped Oil Filled (Yes or No) | By Vendor
15.06 | Option for Oil Fill, Process, and Dress Out | PRICE AS SEPARATE BID ITEM
Additional Comments

## Useful Information
IEEE Std C57.12.00-2006
Table 4, Page 11
Relationships of nominal system voltage to maximum system voltage and basic lightning impulse insulation levels (BIL) for systems 765 kV and below
Nominal System Voltage (kV rms) |  |  |  | Maximum System Voltage (from ANSI C84-1-1995) (kV rms) |  |  | Basic Lightning Impulse Insulation Levels (BIL) in common use (kV crest)
1.2 | [6 empty] | 45 | 30
2.5 | [6 empty] | 60 | 45
5 | [6 empty] | 75 | 60
8.7 | [6 empty] | 95 | 75
15 | [6 empty] | 110 | 95
25 | [6 empty] | 150
34.5 | [6 empty] | 200
46 |  |  |  | 48.3 |  |  | 250 | 200
69 |  |  |  | 72.5 |  |  | 350 | 250
115 |  |  |  | 121 |  |  | 550 | 450 | 350
138 |  |  |  | 145 |  |  | 650 | 550 | 450
161 |  |  |  | 169 |  |  | 750 | 650 | 550
230 |  |  |  | 242 |  |  | 900 | 825 | 750 | 650
345 |  |  |  | 362 |  |  | 1175 | 1050 | 900
500 |  |  |  | 550 |  |  | 1675 | 1550 | 1425 | 1300
765 |  |  |  | 800 |  |  | 2050 | 1925
IEEE Std C57.12.00-2006
Table 14, Page 35
Minimum external clearances between transfomer live parts of different phases of the same voltage
| Nominal System Voltage |  | Maximum System Voltage (from ANSI C84-1-2006, ANSI C92.2-1987) |  | Minimum clearance between live parts of different phases |  |  |  | Minimum clearance between top shed of insulator of bushings of different phases
| (kV rms) |  | (kV rms) |  | Power Transformers |  |  |  | Power Transformers
[5 empty] | mm |  | in |  | mm |  | in
| 1.2 |  |  |  | 51 |  | 2 |  | 25 |  | 1
| 2.5 |  |  |  | 76 |  | 3 |  | 38 |  | 1.5
| 5 |  |  |  | 102 |  | 4 |  | 51 |  | 2
| 8.7 |  |  |  | 127 |  | 5 |  | 64 |  | 2.5
| 15 |  |  |  | 165 |  | 6.5 |  | 89 |  | 3.5
| 25 |  |  |  | 229 |  | 9 |  | 152 |  | 6
| 34.5 |  |  |  | 330 |  | 13 |  | 203 |  | 8
| 46 |  | 48.3 |  | 432 |  | 17 |  | 305 |  | 12
| 69 |  | 72 (ANSI), 72.5 (IEEE) |  | 635 |  | 25 |  | 483 |  | 19
| 115 |  | 121 |  | 1041 |  | 41 |  | 914 |  | 36
| 138 |  | 145 |  | 1245 |  | 49 |  | 1118 |  | 44
| 161 |  | 169 |  | 1448 |  | 57 |  | 1321 |  | 52
| 230 |  | 242 |  | 1778 |  | 70 |  | 1651 |  | 65
| 345 |  | 362 |  | 2286 |  | 90 |  | 2159 |  | 85
| 500 |  | 550 |  | 4064 |  | 160 |  | 3937 |  | 155
| 765 |  | 800 |  | c |  |  |  | c
| 1100 |  | 1200 |  | c |  |  |  | c
IEEE Std C62.11-2005
Table 1, Page 11
Arrester Ratings
Duty-cycle voltage (kV rms) |  |  | Maximum Continuous Operating Voltage MCOV (kV rms) |  |  | Duty-cycle voltage (kV rms) |  |  | Maximum Continuous Operating Voltage MCOV (kV rms)
3 |  |  | 2.55 |  |  | 144 |  |  | 115
6 |  |  | 5.1 |  |  | 168 |  |  | 131
9 |  |  | 7.65 |  |  | 172 |  |  | 140
10 |  |  | 8.4 |  |  | 180 |  |  | 144
12 |  |  | 10.2 |  |  | 192 |  |  | 152
15 |  |  | 12.7 |  |  | 228 |  |  | 180
18 |  |  | 15.3 |  |  | 240 |  |  | 190
21 |  |  | 17 |  |  | 258 |  |  | 209
24 |  |  | 19.5 |  |  | 264 |  |  | 212
27 |  |  | 22 |  |  | 276 |  |  | 220
30 |  |  | 24.4 |  |  | 288 |  |  | 230
36 |  |  | 29 |  |  | 294 |  |  | 235
39 |  |  | 31.5 |  |  | 312 |  |  | 245
45 |  |  | 36.5 |  |  | 396 |  |  | 318
48 |  |  | 39 |  |  | 420 |  |  | 335
54 |  |  | 42 |  |  | 444 |  |  | 353
60 |  |  | 48 |  |  | 468 |  |  | 372
72 |  |  | 57 |  |  | 492 |  |  | 392
90 |  |  | 70 |  |  | 540 |  |  | 428
96 |  |  | 76 |  |  | 564 |  |  | 448
108 |  |  | 84 |  |  | 576 |  |  | 462
120 |  |  | 98 |  |  | 588 |  |  | 470
132 |  |  | 106 |  |  | 612 |  |  | 485
IEEE Std C57.19.100-1995
Table 1, Page 14
Contamination Level |  |  | Typical Environments | [8 empty] | IEEE Std C57.19.100-1995
Page 16
Light |  |  | Areas without industries and with low density of emission-producing residential heating systems. | [8 empty] | Minimum Creep Distance
Areas with some industrial or residential density but subject to frequent winds and/or precipitation.
|  |  | Agricultural areas (exposure to wind-borne fertilizer spray or crop-burning residues can lead to higher contamination levels). | [8 empty] | Contamination | Creep Distance (mm/kV)
|  |  | Mountainous Areas | [8 empty] | Light | 28
|  |  | These areas are not exposed to sea winds or located near the sea. | [8 empty] | Medium | 35
|  |  | Typical measured equilivalent salt deposit density (ESDD) levels are 0.03-0.08 mg/cm^2 | [8 empty] | Heavy | 44
Medium |  |  | Areas with industries not producing highly polluting smoke and/or with average density fo emission-producing residential heating systmes. | [8 empty] | Extra Heavy | 54
Areas with high industrial and/or residential density but subject to frequent winds and/or precipitation.
Areas exposed to sea winds but not located directly on the coast.
Typical measured ESDD levels are 0.08-0.25 mg/cm^2
Heavy |  |  | Areas with high industrial density and large city suburbs with a high density of emission-producing residential heating systems.
Areas close to the sea or exposed to strong sea winds.
Typical measured ESDD levels are 0.25-0.6 mg/cm^2
Extra Heavy |  |  | Small areas subject to industrial smoke-producing thick conductive deposits.
Small coastal areas exposed to very strong and polluting sea winds.
Typcial measured ESDD levels are above 0.6 mg/cm^2.
IEEE Std C57.12.00-2006
Page 7
Cooling Classes of Transformers
First Letter: Internal cooling medium in contact with the windings
O | Mineral Oil or Synthetic Insulating Liquid with Fire Point ≤300 Degrees Celcius
K | Insulating Liquid with Fire Point >300 Degrees Celcius
L | Insulating Liquid with No Measureable Fire Point
Second Letter: Circulation mechanism for internal cooling medium
N | Natural convection flow through cooling equipment and in windings
F | Forced circulation through cooling equipment (I.e., coolant pumps), natural convection flow in the windings (also called nondirected flow)
D | Forced circulation through cooling equipment, directed from the cooling equipment into at least the main windings
Third Letter: External cooling medium
A | Air
W | Water
Fourth Letter: Circulation mechanism for external cooling medium
N | Natural convection
F | Forced circulation [fans (air cooling), pumps (water cooling)]
IEEE Std C57.12.00-2006
Table 2, Page 8
Cooling Class Designation
Present Designation |  |  |  | Previous Designation
ONAN |  |  |  | OA
ONAF |  |  |  | FA
ONAN/ONAF/ONAF |  |  |  | OA/FA/FA
ONAN/ONAF/OFAF |  |  |  | OA/FA/FOA
ONAN/OFAF |  |  |  | OA/FOA
ONAN/ODAF/ODAF |  |  |  | OA/FOAa/FOAa
OFAF |  |  |  | FOA
OFWF |  |  |  | FOW
ODAF |  |  |  | FOAa
ODWF |  |  |  | FOWa
IEEE Std C57.13-1993
Table 7, Page 17
Standard Current Transformer Ratios
Single ratio |  |  |  | Double ratio with series- |  |  |  | Double ratio with taps in
|  |  |  | paralell primary windings |  |  |  | secondary winding
10:5 |  | 800:5 |  | 25 x 50:5 |  |  |  | 25/50:5
15:5 |  | 1200:5 |  | 50 x 100:5 |  |  |  | 50/100:5
25:5 |  | 1500:5 |  | 100 x 200:5 |  |  |  | 100/200:5
40:5 |  | 2000:5 |  | 200 x 400:5 |  |  |  | 200/400:5
50:5 |  | 3000:5 |  | 400 x 800:5 |  |  |  | 300/600:5
75:5 |  | 4000:5 |  | 600 x 1200:5 |  |  |  | 400/800:5
100:5 |  | 5000:5 |  | 1000 x 2000:5 |  |  |  | 600/1200:5
200:5 |  | 6000:5 |  | 2000 x 4000:5 |  |  |  | 1000/2000:5
200:5 |  | 8000:5 | [5 empty] | 1500/3000:5
400:5 |  | 12000:5 | [5 empty] | 2000/4000:5
600:5