## 94.03.12.100
Project: | [5 empty] | Notes
KED #:
Revision:
Date:
SPECIFICATION 842A/94.03.12.100
Isolated Phase Bus Duct
Item | Description | Specified Data | By Bidder | See Note | Rev. #
Specification Summary
This specification covers the design, fabrication, testing and delivery of an isolated phase bus duct system in accordance with this specification and stated Standards.
1 | General Requirements
1.01 | Description | See One-Line
1.02 | CTG 1 Quantity
1.03 | Number of Shipping Splits
1.04 | Maximum Shipping Split length
1.05 | Maximum Support spacing length
1.06 | CTG 2 Quantity
1.07 | Number of Shipping Splits
1.08 | Maximum Shipping Split length
1.09 | Maximum Support spacing length
1.1 | CTG 3 Quantity
1.11 | Number of Shipping Splits
1.12 | Maximum Shipping Split length
1.13 | Maximum Support spacing length
1.14 | STG Quantity
1.15 | Number of Shipping Splits
1.16 | Maximum Shipping Split length
1.17 | Maximum Support spacing length
1.18 | Standard | IEEE C37.23
1.19 | Nominal Operating Voltage (kV rms) | 23.5 |  |  |  | Engineer to enter.
1.2 | Maximum Rated Voltage (kV rms) | 105% of Nominal Operating Voltage
1.21 | Rated BIL (kV) | 150 |  |  |  | 110 for 17kV maximum voltage; 150 for 26kV max voltage; 200 for 36kV max voltage
1.22 | Enclosure Material | Aluminum
1.23 | Bus Material | Aluminum |  |  |  | Aluminum is typical
1.24 | Minimum Rated Continuous Current at 40°C Ambient
1.25 | Main Bus (A rms) | 15000
1.26 | Tapped Bus (A rms) | 2000
1.27 | Conductor Maximum Temperature (°C) | 105 |  |  |  | Standard allows up to 105 degrees C for tin or silver-surfaced bolted joints. May need to specify lower temperature if there is a GCB especially if the GCB has a temperature limitation without derating
1.28 | Enclosure and Support Structure Maximum Temperature (°C) | 80 |  |  |  | Standard allows up to 80 degrees C where enclosure or support structure is accessible to an operating during normal operation. May need to specify 70 degrees C if there is a GCB especially if the GCB has a temperature limitationwithout derating
1.29 | Rated Momentary Withstand Current
1.3 | Main Bus (kA rms asymmetrical) | 223 |  |  |  | See ETAP.
1.31 | Tapped Bus (kA rms asymmetrical) | 223 |  |  |  | Tapped bus must be rated to handle total fault current (system + generator)
1.32 | Rated Short-Time Withstand Current
1.33 | Main Bus (kA rms asymmetrical) | 135 |  |  |  | See ETAP.
1.34 | Tapped Bus (kA rms asymmetrical) | 135 |  |  |  | Tapped bus must be rated to handle total fault current (system + generator)
1.35 | Design Phase-to-Phase Spacing (in.) | See Isophase Bus Duct Layout
1.36 | Typical Centerline Height above Grade | See Isophase Bus Duct Layout
1.37 | Color | ANSI 61 Light Gray
1.38 | Frequency (Hz) | 60
2 | Quantities per Set
2.01 | Length (3-Phase feet) | See Isophase Bus Duct Layout |  |  |  | Engineer to enter mark up design drawing to include all quantities listed below including fire wall penetrations
2.02 | Quantity of 3-Phase 90° Vertical Elbows | See Isophase Bus Duct Layout
2.03 | Quantity of 3-Phase 90° Horizontal Elbows | See Isophase Bus Duct Layout
2.04 | Quantity of 3-Phase Taps | See Isophase Bus Duct Layout
2.05 | Quantity of Wall Penetrations (Not Fire Rated) | See Isophase Bus Duct Layout
2.06 | Quantity of Wall Penetrations (Fire Rated) | See Isophase Bus Duct Layout
2.07 | Quantity of 3-Phase Phase Spacing Transitions | See Isophase Bus Duct Layout
3 | Terminations
3.01 | Generator Step-Up Transformer | See Isophase Bus Duct Layout
3.02 | Generator | See Isophase Bus Duct Layout
3.03 | Auxiliary Transformer | See Isophase Bus Duct Layout
3.04 | Surge/VT Cubicle | See Isophase Bus Duct Layout
3.05 | Excitation Transformer | See Isophase Bus Duct Layout
4 | Condensation Control
4.01 | Condensation Control Method | Space Heaters |  |  |  | Space heaters is recommeded. Pressurized Air is more expensive. If Owner RFP calls out Air, clarify or include VE item analysis to move to space heaters.
4.02 | Space Heaters
4.03 | Quantity of Space Heaters
4.04 | Rated Voltage of Space Heaters (V rms) | 240
4.05 | Energization Voltage of Space Heaters (V rms) | 120
4.06 | Dry Pressurized Air with Seal-Off Bushings
4.07 | Air Source | N/A |  |  |  | Inform Mechanical if pressurized air is used as base bid. They will need to bring the plant air system to the ISBD.
4.08 | Minimum Pressure (psig) | N/A
4.09 | Maximum Air Flow (cfm) | N/A
4.1 | Generator Circuit Breaker | N/A
5 | Additional Items
5.01 | Solar Radiation Shield | As Required
5.02 | Support Steel for Isolated Phase Bus Duct (Vendor to provide # of tons of steel) (Contractors firewall structure shall not be incorporated in the support system) | Included |  |  |  | Verify support steel is not carried by structural
5.03 | Support Steel for Generator Circuit Breaker (Vendor to provide # of tons of steel) (Contractors firewall structure shall not be incorporated in the support system) | Included |  |  |  | Verify support steel is not carried by structural or GCB vendor
5.04 | Support Steel for Generator Terminal Enclosure | Included |  |  |  | Verify OEM scope. Typically provided by OEM unless it’s a GE 7HA single shaft
6 | Spare Parts
6.01 | Manufacturer Recommended Start-Up Spare Parts | Include
6.02 | Manufacturer Recommended Two-Year Spare Parts | Do Not Include
7 | Drawings Supplied as part of this Specification
7.01 | General Arrangement | No
7.02 | One-Line Diagram | No
7.03 | Isophase Routing | Yes
8 | Additional Data to be supplied by Vendor
8.01 | Enclosure Outside Diameter (inches)
8.02 | Average Assembled Weight (lbs/3-phase ft)
8.03 | Support Steel (tons)
8.04 | Total Loss per 3-Phase Foot (watts) at rated current
8.05 | Add/Deduct Pricing
8.06 | Main Bus
8.07 | Linear 3-Phase Foot ($/ft)
8.08 | Single-Phase Horizontal Elbow ($/ea)
8.09 | Single-Phase Vertical Elbow ($/ea)
8.1 | 3-Phase Phase Spacing Transition ($/ea)
8.11 | 3-Phase Seal-Off Bushing ($/ea)
8.12 | Tapped Bus
8.13 | Linear 3-Phase Foot ($/ft)
8.14 | Single-Phase Horizontal Elbow ($/ea)
8.15 | Single-Phase Vertical Elbow ($/ea)
8.16 | 3-Phase Phase Spacing Transition ($/ea)
8.17 | 3-Phase Seal-Off Bushing ($/ea)
8.18 | Non-Fire-Rated 3-Phase Wall Transition ($/ea)
8.19 | 2-Hour Fire-Rated 3-Phase Wall Transition ($/ea)
8.2 | 3-Phase Equipment Termination ($/ea)
9 | Additional Comments
9.01 | Vendor to provide all fire stop material (internal and external at the penetration) and fire wall penetration equipment