## Instructions
Instructions and Comments
Commercial Bid Form Tab
1. Submit this form to Bidders for quotes | Hard Entered Data
2. Use these quotes and fill out the QCS page | Drop Down
Calculation
Data Setup Tab
1. Fill out Project Name and the required Project Details
2. Per each type of equipment, select the comparable job needed to determine Vendor Pipe Heater Length
3. From Section 1-B, input the Site Specific Ambient Temperature (°F)
4. FIl out the circuits quantity tab with the quantity of heated enclosures, Tube bundle, safety showers e.t.c
5. Copy and Paste pipe data into Pipe Data Table into the corresponding columns. NOTE: Ambient Temp column will auto-populated with the value inputted in Step 3
6. Refresh Data to perform calculations needed to populate the sheet in the Quote Sheet tab
Quote Sheet Tab - Adjustable Data (Yellow Cells)
1. "Conduit" can be modified if necessary by changing the average linear foot of condiut assigned to each circuit
Default is set at 30 LF per circuit. NOTE: Be sure to include UOM when altering
2. "Wire" can be modified if necessary by changing the average linear foot of wire assigned to each circuit
Default is set at 40 LF per circuit, note that wire/cable length should be 10 LF longer than conduit length. NOTE: Be sure to include UOM when altering
3. "Terms" can be modified if necessary by changing the number of terms assigned to each circuit
Default is set at 6 EA per circuit. NOTE: Be sure to include UOM when altering
4. DO NOT change formulas in GOLD cells
Quote Sheet Tab - Adjustable Data (Light-Green Cells)
1. Only update every 6 MONTHS
2. Choose the lowest TOTAL price from Heat Trace Materials and Electrical Equipment.
3. To select the lowest Bidder select the number 1 through 3 that corresponds with the low Bidder into the ORANGE cells
4. DO NOT change formulas in GOLD cells
QCS Tab
1. Use the LDR to determine the UR and OUM for Self Perfrom Labor Pricing
2. Use informtaion from Bidders to fill out the pricing and any other information necessary.

## Reference Pictures
Typical Heat Trace System Components | Typical Heat Trace Cable Allowances |  | Typical Heat Trace Configuration
| Heat Trace Around Flange | Heat Trace Around Valve
| Heat Trace Around Pump | Heat Trace Around Support

## Data Setup
Project Name
Project Details
Job Configuraiton | 2x1
Aux Boiler QTY | 0
ACC Cells | 0
BFP QTY | 0
Condenser QTY | 0
Vendor Pipe Comparables | [8 empty] | Circuit QTY
Type | Location | Project | Job Configuration | Circuits (EA) | SR Cable QTY (LF) | MI Cable QTY (LF) | Total Cable (LF) |  | Component | Quantity (EA) | Circuit QTY
ACC | Outdoor | Cove Point | 2x2 | 0 | 0 | 0 | 0 |  | Vendor Pipe | 80 | 361
Aux Boiler | Outdoor | Woodbridge | 2x1 | 0 | 0 | 0 | 0 |  | BOP | 281
BFP | Outdoor | Woodbridge | 2x1 | 0 | 0 | 0 | 0 |  | Heated Enclosures | 0
Condenser | Outdoor | Woodbridge | 2x1 | 0 | 0 | 0 | 0 |  | Tube Bundles | 0
CTG | Indoor | Woodbridge | 2x1 | 0 | 0 | 0 | 0 |  | Sample and Chem Feed Lines | 0
HRSG | Outdoor | Woodbridge | 2x1 | 80 | 0 | 10708 | 10708 |  | Safety Showers | 0
STG | Indoor | Woodbridge | 2x1 | 0 | 0 | 0 | 0 |  | Specialty Valves | 0
Totals |  |  |  | 80 | 0 | 10708 | 10708 |  | Condensate Pots | 0
Minimum Site Specific Ambient Temperature (°F) |  | -8
Pipe Data Table
Sheet # | Line Number | Service | Size NPS | Final Schedule | Material | Design Temp (°F) | Operating Temp (°F) | System Code | Pipe Length (LF) | Area | Insulation Thickness (in) | Insulation Type | Flanges | Valves | Pipe Support | Ambient Temp (°F)
CWT | 12"-CWT101-ABB 1"A-Y |  | 12 | std wt | CS | 225 |  | CWT | 109 | 14 | 1 | A | 10 | 4 | 8 | -8
PS-020 | 2"-HPS103-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 8 | 4.5 | B | 0 | 4 | 1 | -8
PS-020 | 2"-HPS103-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 9 | 4.5 | B | 0 | 4 | 1 | -8
PS-020 | 2"-HPS105-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 8 | 4.5 | B | 0 | 4 | 1 | -8
PS-020 | 2"-HPS105-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 9 | 4.5 | B | 0 | 4 | 1 | -8
PS-020 | 3"-HPS103-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 8 | 5 | B | 0 | 0 | 0 | -8
PS-020 | 3"-HPS103-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 9 | 5 | B | 0 | 0 | 0 | -8
PS-020 | 3"-HPS105-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 8 | 5 | B | 0 | 0 | 0 | -8
PS-020 | 3"-HPS105-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 9 | 5 | B | 0 | 0 | 0 | -8
PS-020 | 6"-HPS103-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 2 | 8 | 6 | B | 0 | 0 | 0 | -8
PS-020 | 6"-HPS103-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 2 | 9 | 6 | B | 0 | 0 | 0 | -8
PS-020 | 6"-HPS105-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 4 | 8 | 6 | B | 0 | 0 | 0 | -8
PS-020 | 6"-HPS105-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 4 | 9 | 6 | B | 0 | 0 | 0 | -8
PS-021 | 2"-HPS115-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 8 | 4.5 | B | 0 | 4 | 1 | -8
PS-021 | 2"-HPS115-BHD 4.5"B-Y | Steam | 2 | SCH 160 | P91 | 1100 | 1056 | HPS | 6 | 9 | 4.5 | B | 0 | 4 | 1 | -8
PS-021 | 3"-HPS115-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 8 | 5 | B | 0 | 0 | 0 | -8
PS-021 | 3"-HPS115-BHD 5"B-Y | Steam | 3 | SCH 160 | P91 | 1100 | 1056 | HPS | 1 | 9 | 5 | B | 0 | 0 | 0 | -8
PS-021 | 6"-HPS115-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 4 | 8 | 6 | B | 0 | 0 | 0 | -8
PS-021 | 6"-HPS115-BHD 6"B-Y | Steam | 6 | .6796 | P91 | 1100 | 1056 | HPS | 4 | 9 | 6 | B | 0 | 0 | 0 | -8
PS-032 | 10"-HRH100-BED 7"B-Y | Steam | 10 | sch 40 | P91 | 1100 | 1053 | HRH | 4 | 8 | 7 | B | 0 | 0 | 0 | -8
PS-032 | 10"-HRH100-BED 7"B-Y | Steam | 10 | sch 40 | P91 | 1100 | 1053 | HRH | 4 | 9 | 7 | B | 0 | 0 | 0 | -8
PS-032 | 10"-HRH107-BED 7"B-Y | Steam | 10 | sch 40 | P91 | 1100 | 1053 | HRH | 5 | 6 | 7 | B | 0 | 0 | 0 | -8
PS-032 | 10"-HRH107-BED 7"B-Y | Steam | 10 | sch 40 | P91 | 1100 | 1053 | HRH | 5 | 7 | 7 | B | 0 | 0 | 0 | -8
PS-032 | 18"-HRH100-BED 8"B-Y | Steam | 18 | XS | P91 | 1100 | 1053 | HRH | 269 | 8 | 8 | B | 6 | 0 | 8 | -8
PS-032 | 18"-HRH100-BED 8"B-Y | Steam | 18 | XS | P91 | 1100 | 1053 | HRH | 269 | 9 | 8 | B | 6 | 0 | 8 | -8
PS-032 | 2"-HRH100-BED 4.5"B-Y | Steam | 2 | sch 80 | P91 | 1100 | 1053 | HRH | 5 | 8 | 4.5 | B | 0 | 3 | 1 | -8
PS-032 | 2"-HRH100-BED 4.5"B-Y | Steam | 2 | sch 80 | P91 | 1100 | 1053 | HRH | 5 | 9 | 4.5 | B | 0 | 3 | 1 | -8
PS-032 | 2"-HRH107-BED 4.5"B-Y | Steam | 2 | sch 80 | P91 | 1100 | 1053 | HRH | 9 | 6 | 4.5 | B | 0 | 6 | 2 | -8
PS-032 | 2"-HRH107-BED 4.5"B-Y | Steam | 2 | sch 80 | P91 | 1100 | 1053 | HRH | 9 | 7 | 4.5 | B | 0 | 6 | 2 | -8
PS-032 | 3"-HRH100-BED 5"B-Y | Steam | 3 | sch 40 | P91 | 1100 | 1053 | HRH | 1 | 8 | 5 | B | 0 | 0 | 0 | -8
PS-032 | 3"-HRH100-BED 5"B-Y | Steam | 3 | sch 40 | P91 | 1100 | 1053 | HRH | 1 | 9 | 5 | B | 0 | 0 | 0 | -8
PS-032 | 3"-HRH107-BED 5"B-Y | Steam | 3 | sch 40 | P91 | 1100 | 1053 | HRH | 2 | 6 | 5 | B | 0 | 0 | 0 | -8
PS-032 | 3"-HRH107-BED 5"B-Y | Steam | 3 | sch 40 | P91 | 1100 | 1053 | HRH | 2 | 7 | 5 | B | 0 | 0 | 0 | -8
PS-040 | 2"-LPS103-ABA 2"B-Y | Steam | 2 | sch 80 | CS | 750 | 625 | LPS | 4 | 8 | 2 | B | 0 | 3 | 1 | -8
PS-040 | 2"-LPS103-ABA 2"B-Y | Steam | 2 | sch 80 | CS | 750 | 625 | LPS | 3 | 9 | 2 | B | 0 | 3 | 1 | -8
PS-040 | 3"-LPS103-ABA 2.5"B-Y | Steam | 3 | sch 40 | CS | 750 | 625 | LPS | 1 | 8 | 2.5 | B | 0 | 0 | 0 | -8
PS-040 | 3"-LPS103-ABA 2.5"B-Y | Steam | 3 | sch 40 | CS | 750 | 625 | LPS | 1 | 9 | 2.5 | B | 0 | 0 | 0 | -8
PS-040 | 8"-LPS103-ABA 3"B-Y | Steam | 8 | sch 40 | CS | 750 | 625 | LPS | 4 | 8 | 3 | B | 0 | 0 | 0 | -8
PS-040 | 8"-LPS103-ABA 3"B-Y | Steam | 8 | sch 40 | CS | 750 | 625 | LPS | 4 | 9 | 3 | B | 0 | 0 | 0 | -8
PS-052 | 1"-CND06-ADA 1"A-Y | Water | 1 | sch 80 | CS | 750 | 140 | CND | 1 | 8 | 1 | A | 0 | 0 | 0 | -8
PS-052 | 1"-CND06-ADA 1"A-Y | Water | 1 | sch 80 | CS | 750 | 140 | CND | 1 | 9 | 1 | A | 0 | 0 | 0 | -8
PS-052 | 10"-CND06-ADA 1"A-Y | Water | 10 | sch 40 | CS | 750 | 140 | CND | 50 | 8 | 1 | A | 0 | 0 | 2 | -8
PS-052 | 10"-CND06-ADA 1"A-Y | Water | 10 | sch 40 | CS | 750 | 140 | CND | 50 | 9 | 1 | A | 0 | 0 | 2 | -8
PS-052 | 2"-CND11-ADA 1"A-Y | Water | 2 | sch 80 | CS | 750 | 140 | CND | 78 | 8 | 1 | A | 10 | 0 | 9 | -8
PS-052 | 2"-CND11-ADA 1"A-Y | Water | 2 | sch 80 | CS | 750 | 140 | CND | 78 | 9 | 1 | A | 10 | 0 | 9 | -8
PS-052 | 4"-CND06-ADA 1"A-Y | Water | 4 | sch 40 | CS | 750 | 140 | CND | 1 | 8 | 1 | A | 0 | 0 | 0 | -8
PS-052 | 4"-CND06-ADA 1"A-Y | Water | 4 | sch 40 | CS | 750 | 140 | CND | 1 | 9 | 1 | A | 0 | 0 | 0 | -8
PS-052 | 8"-CND06-ADA 1"A-Y | Water | 8 | sch 40 | CS | 750 | 140 | CND | 224 | 8 | 1 | A | 7 | 0 | 15 | -8
PS-052 | 8"-CND06-ADA 1"A-Y | Water | 8 | sch 40 | CS | 750 | 140 | CND | 224 | 9 | 1 | A | 7 | 0 | 15 | -8
PS-060,061,062 | 0.75"-BFW510-AHB 1.5"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 1 | 8 | 1.5 | A | 0 | 4 | 0 | -8
PS-060,061,062 | 0.75"-BFW510-AHB 1.5"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 1 | 9 | 1.5 | A | 0 | 4 | 0 | -8
PS-060,061,062 | 0.75"-BFW510-AHB 2"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 10 | 8 | 2 | A | 0 | 24 | 0 | -8
PS-060,061,062 | 0.75"-BFW510-AHB 2"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 10 | 9 | 2 | A | 0 | 24 | 0 | -8
PS-060,061,062 | 0.75"-BFW512-AHB 1.5"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 3 | 8 | 1.5 | A | 0 | 6 | 0 | -8
PS-060,061,062 | 0.75"-BFW512-AHB 1.5"A-Y | Water/Steam | 0.75 | sch 160 | CS | 745 | 400 | BFW | 3 | 9 | 1.5 | A | 0 | 6 | 0 | -8
PS-060,061,062 | 1"-BFW510-AHB 1.5"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 2 | 8 | 1.5 | A | 0 | 4 | 0 | -8
PS-060,061,062 | 1"-BFW510-AHB 1.5"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 2 | 9 | 1.5 | A | 0 | 4 | 0 | -8
PS-060,061,062 | 1"-BFW510-AHB 2"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 6 | 8 | 2 | A | 0 | 12 | 0 | -8
PS-060,061,062 | 1"-BFW510-AHB 2"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 6 | 9 | 2 | A | 0 | 12 | 0 | -8
PS-060,061,062 | 1"-BFW511-AHB 2"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 6 | 8 | 2 | A | 0 | 10 | 0 | -8
PS-060,061,062 | 1"-BFW511-AHB 2"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 6 | 9 | 2 | A | 0 | 10 | 0 | -8
PS-060,061,062 | 1"-BFW512-AHB 1.5"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 76 | 8 | 1.5 | A | 9 | 8 | 15 | -8
PS-060,061,062 | 1"-BFW512-AHB 1.5"A-Y | Water/Steam | 1 | sch 160 | CS | 745 | 400 | BFW | 76 | 9 | 1.5 | A | 9 | 8 | 15 | -8
PS-060,061,062 | 1.5"-BFW510-AHB 1.5"A-Y | Water/Steam | 1.5 | sch 160 | CS | 745 | 400 | BFW | 74 | 8 | 1.5 | A | 5 | 2 | 10 | -8
PS-060,061,062 | 1.5"-BFW510-AHB 1.5"A-Y | Water/Steam | 1.5 | sch 160 | CS | 745 | 400 | BFW | 76 | 9 | 1.5 | A | 5 | 2 | 10 | -8
PS-060,061,062 | 1.5"-BFW511-AHB 2"A-Y | Water/Steam | 1.5 | sch 160 | CS | 745 | 400 | BFW | 147 | 8 | 2 | A | 10 | 4 | 16 | -8
PS-060,061,062 | 1.5"-BFW511-AHB 2"A-Y | Water/Steam | 1.5 | sch 160 | CS | 745 | 400 | BFW | 147 | 9 | 2 | A | 10 | 4 | 16 | -8
PS-060,061,062 | 2"-BFW510-AHB 2"A-Y | Water/Steam | 2 | sch 160 | CS | 745 | 400 | BFW | 8 | 8 | 2 | A | 2 | 3 | 0 | -8
PS-060,061,062 | 2"-BFW510-AHB 2"A-Y | Water/Steam | 2 | sch 160 | CS | 745 | 400 | BFW | 8 | 9 | 2 | A | 2 | 3 | 0 | -8
PS-060,061,062 | 2"-BFW512-AHB 1.5"A-Y | Water/Steam | 2 | sch 160 | CS | 745 | 400 | BFW | 3 | 8 | 1.5 | A | 0 | 2 | 0 | -8
PS-060,061,062 | 2"-BFW512-AHB 1.5"A-Y | Water/Steam | 2 | sch 160 | CS | 745 | 400 | BFW | 3 | 9 | 1.5 | A | 0 | 2 | 0 | -8
PS-060,061,062 | 2.5"-BFW510-AHB 1.5"A-Y | Water/Steam | 2.5 | sch 160 | CS | 745 | 400 | BFW | 1 | 8 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 2.5"-BFW510-AHB 1.5"A-Y | Water/Steam | 2.5 | sch 160 | CS | 745 | 400 | BFW | 1 | 9 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 3"-BFW511-AHB 2"A-Y | Water/Steam | 3 | sch 160 | CS | 745 | 400 | BFW | 1 | 8 | 2 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 3"-BFW511-AHB 2"A-Y | Water/Steam | 3 | sch 160 | CS | 745 | 400 | BFW | 1 | 9 | 2 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 3"-BFW512-AHB 1.5"A-Y | Water/Steam | 3 | sch 160 | CS | 745 | 400 | BFW | 138 | 8 | 1.5 | A | 12 | 12 | 11 | -8
PS-060,061,062 | 3"-BFW512-AHB 1.5"A-Y | Water/Steam | 3 | sch 160 | CS | 745 | 400 | BFW | 140 | 9 | 1.5 | A | 12 | 12 | 11 | -8
PS-060,061,062 | 4"-BFW510-AHB 1.5"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 2 | 8 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 4"-BFW510-AHB 1.5"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 2 | 9 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 4"-BFW511-AHB 2"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 4 | 8 | 2 | A | 0 | 2 | 0 | -8
PS-060,061,062 | 4"-BFW511-AHB 2"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 4 | 9 | 2 | A | 0 | 2 | 0 | -8
PS-060,061,062 | 4"-BFW512-AHB 1.5"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 1 | 8 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 4"-BFW512-AHB 1.5"A-Y | Water/Steam | 4 | sch 160 | CS | 745 | 400 | BFW | 1 | 9 | 1.5 | A | 0 | 0 | 0 | -8
PS-060,061,062 | 6"-BFW511-AHB 2"A-Y | Water/Steam | 6 | XXS | CS | 745 | 400 | BFW | 140 | 8 | 2 | A | 8 | 4 | 12 | -8
PS-060,061,062 | 6"-BFW511-AHB 2"A-Y | Water/Steam | 6 | XXS | CS | 745 | 400 | BFW | 140 | 9 | 2 | A | 8 | 4 | 12 | -8
PS-060,061,062 | 8"-BFW510-AHB 2"A-Y | Water/Steam | 8 | .945 | CS | 745 | 400 | BFW | 88 | 8 | 2 | A | 3 | 0 | 4 | -8
PS-060,061,062 | 8"-BFW510-AHB 2"A-Y | Water/Steam | 8 | .945 | CS | 745 | 400 | BFW | 88 | 9 | 2 | A | 3 | 0 | 4 | -8
PS-060,061,063 | 0.75"-BFW505-AEA 1.5"A-Y | Water/Steam | 0.75 | sch 80 | CS | 775 | 400 | BFW | 3 | 9 | 1.5 | A | 0 | 3 | 0 | -8
PS-060,061,063 | 0.75"-BFW505-AEA 2"A-Y | Water/Steam | 0.75 | sch 80 | CS | 775 | 400 | BFW | 12 | 9 | 2 | A | 0 | 21 | 0 | -8
PS-060,061,063 | 1"-BFW505-AEA 1.5"A-Y | Water/Steam | 1 | sch 80 | CS | 775 | 400 | BFW | 87 | 9 | 1.5 | A | 12 | 7 | 18 | -8
PS-060,061,063 | 1"-BFW505-AEA 2"A-Y | Water/Steam | 1 | sch 80 | CS | 775 | 400 | BFW | 3 | 9 | 2 | A | 0 | 3 | 0 | -8
PS-060,061,063 | 2"-BFW505-AEA 1.5"A-Y | Water/Steam | 2 | sch 80 | CS | 775 | 400 | BFW | 4 | 9 | 1.5 | A | 0 | 4 | 0 | -8
PS-060,061,063 | 3"-BFW505-AEA 2"A-Y | Water/Steam | 3 | sch 40 | CS | 775 | 400 | BFW | 302 | 9 | 2 | A | 22 | 12 | 34 | -8
PS-060,061,063 | 4"-BFW505-AEA 1.5"A-Y | Water/Steam | 4 | sch 40 | CS | 775 | 400 | BFW | 3 | 9 | 1.5 | A | 0 | 0 | 0 | -8
PS-090 | 2"-BDN101-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 15 | 4 | 1 | A | 2 | 2 | 2 | -8
PS-090 | 2"-BDN103-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 8 | 4 | 1 | A | 2 | 1 | 0 | -8
PS-090 | 2"-BDN103-ABA 1.5"B-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 8 | 4 | 1.5 | B | 0 | 6 | 0 | -8
PS-090 | 4"-BDN103-ABA 1.5"B-Y | Water/Steam | 4 | sch 40 | CS | 750 | 680 | BDN | 5 | 4 | 1.5 | B | 0 | 0 | 1 | -8
PS-091 | 3"-BDN105-ABA 1"A-Y | Water/Steam | 3 | sch 40 | CS | 750 | 680 | BDN | 1 | 4 | 1 | A | 0 | 0 | 0 | -8
PS-091 | 4"-BDN105-ABA 1"A-Y | Water/Steam | 4 | sch 40 | CS | 750 | 680 | BDN | 21 | 4 | 1 | A | 3 | 4 | 3 | -8
PS-091 | 6"-BDN105-ABA 1"A-Y | Water/Steam | 6 | sch 40 | CS | 750 | 680 | BDN | 8 | 4 | 1 | A | 1 | 0 | 1 | -8
PS-091 | 8"-BDN102-CBA 1"A-Y | Water/Steam | 8 | sch 10S | SS | 115 | 680 | BDN | 18 | 4 | 1 | A | 5 | 0 | 2 | -8
PS-095 | 2"-BDN109-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 13 | 5 | 1 | A | 2 | 2 | 2 | -8
PS-095 | 2"-BDN111-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 8 | 5 | 1 | A | 2 | 1 | 0 | -8
PS-095 | 2"-BDN111-ABA 1.5"B-Y | Water/Steam | 2 | sch 80 | CS | 750 | 680 | BDN | 8 | 5 | 1.5 | B | 0 | 6 | 0 | -8
PS-095 | 4"-BDN111-ABA 1.5"B-Y | Water/Steam | 4 | sch 40 | CS | 750 | 680 | BDN | 5 | 5 | 1.5 | B | 0 | 0 | 1 | -8
PS-096 | 3"-BDN113-ABA 1"A-Y | Water/Steam | 3 | sch 40 | CS | 750 | 680 | BDN | 1 | 5 | 1 | A | 0 | 0 | 0 | -8
PS-096 | 4"-BDN113-ABA 1"A-Y | Water/Steam | 4 | sch 40 | CS | 750 | 680 | BDN | 21 | 5 | 1 | A | 3 | 4 | 2 | -8
PS-096 | 6"-BDN113-ABA 1"A-Y | Water/Steam | 6 | sch 40 | CS | 750 | 680 | BDN | 8 | 5 | 1 | A | 1 | 0 | 1 | -8
PS-096 | 8"-BDN110-CBA 1"A-Y | Water/Steam | 8 | sch 10S | SS | 115 | 680 | BDN | 18 | 5 | 1 | A | 5 | 0 | 2 | -8
PS-120 | 2"-AXS101-ADA 1.5"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 2 | 13 | 1.5 | A | 0 | 2 | 1 | -8
PS-120 | 4"-AXS101-ADA 1.5"A-Y | Water/Steam | 4 | sch 40 | CS | 750 | 475 | AXS | 4 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-121 | 3"-CND12-ADA 1"A-Y | Water | 3 | sch 40 | CS | 750 | 140 | CND | 43 | 8 | 1 | A | 10 | 11 | 2 | -8
PS-121 | 3"-CND12-ADA 1"A-Y | Water | 3 | sch 40 | CS | 750 | 140 | CND | 35 | 9 | 1 | A | 10 | 5 | 2 | -8
PS-123 | 1"-AXS122-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 6 | 8 | 1 | A | 2 | 1 | 0 | -8
PS-123 | 1"-AXS122-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 6 | 9 | 1 | A | 2 | 1 | 0 | -8
PS-123 | 1"-AXS124-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 8 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 1"-AXS124-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 9 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 1"-AXS125-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 1 | 8 | 1 | A | 0 | 1 | 0 | -8
PS-123 | 1"-AXS125-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 1 | 9 | 1 | A | 0 | 1 | 0 | -8
PS-123 | 1"-AXS127-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 8 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 1"-AXS127-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 9 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 1"-AXS128-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 1 | 8 | 1 | A | 0 | 1 | 0 | -8
PS-123 | 1"-AXS128-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 1 | 9 | 1 | A | 0 | 1 | 0 | -8
PS-123 | 1"-AXS130-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 8 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 1"-AXS130-ABA 1"A-Y | Water/Steam | 1 | sch 80 | CS | 750 | 475 | AXS | 7 | 9 | 1 | A | 2 | 1 | 1 | -8
PS-123 | 2"-AXS122-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 8 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS122-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 9 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS124-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 43 | 8 | 1 | A | 7 | 2 | 5 | -8
PS-123 | 2"-AXS124-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 42 | 9 | 1 | A | 7 | 2 | 5 | -8
PS-123 | 2"-AXS125-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 8 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS125-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 9 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS127-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 52 | 8 | 1 | A | 7 | 2 | 6 | -8
PS-123 | 2"-AXS127-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 51 | 9 | 1 | A | 7 | 2 | 6 | -8
PS-123 | 2"-AXS128-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 8 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS128-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 10 | 9 | 1 | A | 3 | 2 | 1 | -8
PS-123 | 2"-AXS130-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 72 | 8 | 1 | A | 7 | 2 | 9 | -8
PS-123 | 2"-AXS130-ABA 1"A-Y | Water/Steam | 2 | sch 80 | CS | 750 | 475 | AXS | 72 | 9 | 1 | A | 7 | 2 | 9 | -8
PS-260 | 2"-CWS107-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 37 | 14 |  |  | 8 | 2 | 4 | -8
PS-260 | 2"-CWS108-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 35 | 14 |  |  | 8 | 2 | 0 | -8
PS-260 | 2"-CWS109-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 35 | 14 |  |  | 8 | 2 | 0 | -8
PS-260 | 2"-CWS110-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 35 | 14 |  |  | 8 | 2 | 0 | -8
PS-260 | 2"-CWS111-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 35 | 14 |  |  | 8 | 2 | 0 | -8
PS-260 | 2"-CWS112-AMA "-Y | Water | 2 | sch 80 | CS | 775 | 140 | CWS | 35 | 14 |  |  | 8 | 2 | 0 | -8
PS-330 | 2"-CTP17-CBA 1"A-Y | Water | 2 | sch 40S | SS | 115 | 225 | CTP | 7 | 2 | 1 | A | 2 | 0 | 1 | -8
PS-330 | 2"-CTP17-CBA 1"A-Y | Water | 2 | sch 40S | SS | 115 | 225 | CTP | 7 | 3 | 1 | A | 2 | 0 | 1 | -8
PS-330 | 2.5"-CTP16-CBA 1"A-Y | Water | 2.5 | sch 10S | SS | 115 | 225 | CTP | 2 | 2 | 1 | A | 1 | 0 | 0 | -8
PS-330 | 2.5"-CTP16-CBA 1"A-Y | Water | 2.5 | sch 10S | SS | 115 | 225 | CTP | 2 | 3 | 1 | A | 1 | 0 | 0 | -8
PS-330 | 2.5"-CTP17-CBA 1"A-Y | Water | 2.5 | sch 10S | SS | 115 | 225 | CTP | 18 | 2 | 1 | A | 1 | 0 | 4 | -8
PS-330 | 2.5"-CTP17-CBA 1"A-Y | Water | 2.5 | sch 10S | SS | 115 | 225 | CTP | 18 | 3 | 1 | A | 1 | 0 | 3 | -8
PS-332 | 0.5"-TCF17-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 9 | 14 | 1 | C | 5 | 1 | 3 | -8
PS-332 | 1"-TCF17-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-332 | 2"-TCF19-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 3 | 14 | 1 | C | 1 | 1 | 0 | -8
PS360 | 12"-RWS1000-ABA 1"A-Y | Water | 12 | std wt | CS | 750 | 105 | RWS | 143 | 13 | 1 | A | 9 | 9 | 7 | -8
PS360 | 12"-RWS2000-ABA 1"A-Y | Water | 12 | std wt | CS | 750 | 105 | RWS | 222 | 14 | 1 | A | 12 | 3 | 10 | -8
PS360 | 16"-RWS1000-ABA 1"A-Y | Water | 16 | std wt | CS | 750 | 105 | RWS | 10 | 13 | 1 | A | 0 | 0 | 0 | -8
PS360 | 16"-RWS2000-ABA 1"A-Y | Water | 16 | std wt | CS | 750 | 105 | RWS | 4 | 14 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 1.5"-PWS11-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 10 | 12 | 1 | A | 6 | 0 | 2 | -8
PS-400 | 1.5"-PWS12-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 5 | 4 | 1 | A | 3 | 0 | 1 | -8
PS-400 | 1.5"-PWS15-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 5 | 5 | 1 | A | 3 | 0 | 1 | -8
PS-400 | 1.5"-PWS20-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 5 | 14 | 1 | A | 3 | 0 | 1 | -8
PS-400 | 1.5"-PWS21-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 5 | 14 | 1 | A | 3 | 0 | 1 | -8
PS-400 | 1.5"-PWS22-ABK 1"A-Y | Water | 1.5 | CALC | CS | 200 | 105 | PWS | 5 | 14 | 1 | A | 3 | 0 | 1 | -8
PS-400 | 2"-PWS10-ABK 1"A-Y | Water | 2 | CALC | CS | 200 | 105 | PWS | 11 | 10 | 1 | A | 3 | 0 | 2 | -8
PS-400 | 2.5"-PWS11-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 1 | 12 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 2.5"-PWS12-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 0 | 4 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 2.5"-PWS15-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 0 | 5 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 2.5"-PWS20-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 0 | 14 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 2.5"-PWS21-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 0 | 14 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 2.5"-PWS22-ABK 1"A-Y | Water | 2.5 | CALC | CS | 200 | 105 | PWS | 0 | 14 | 1 | A | 0 | 0 | 0 | -8
PS-400 | 4"-PWS10-ABK 1"A-Y | Water | 4 | CALC | CS | 200 | 105 | PWS | 20 | 10 | 1 | A | 2 | 0 | 2 | -8
PS-410 | 0.75"-DWS101-CBA 1.5"A-Y | Water | 0.75 | sch 40S | SS | 115 | 105 | DWS | 3 | 13 | 1.5 | A | 0 | 1 | 1 | -8
PS-410 | 0.75"-DWS102-CBA 1.5"A-Y | Water | 0.75 | sch 40S | SS | 115 | 105 | DWS | 3 | 13 | 1.5 | A | 0 | 1 | 1 | -8
PS-410 | 2"-DWS101-CBA 1.5"A-Y | Water | 2 | sch 40S | SS | 115 | 105 | DWS | 1 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-410 | 2"-DWS102-CBA 1.5"A-Y | Water | 2 | sch 40S | SS | 115 | 105 | DWS | 1 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-410 | 4"-DWS103-CDA 1.5"A-Y | Water | 4 | sch 40S | SS | 300 | 105 | DWS | 38 | 13 | 1.5 | A | 3 | 2 | 1 | -8
PS-410 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 32 | 13 | 1.5 | A | 2 | 4 | 3 | -8
PS-411 | 0.5"-DWS104-CBD 1.5"A-Y | Water | 0.5 | sch 40S | SS | 130 | 105 | DWS | 1 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-411 | 0.75"-DWS104-CBD 1.5"A-Y | Water | 0.75 | sch 40S | SS | 130 | 105 | DWS | 58 | 13 | 1.5 | A | 8 | 34 | 6 | -8
PS-411 | 1"-DWS104-CBD 1.5"A-Y | Water | 1 | sch 40S | SS | 130 | 105 | DWS | 1 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-411 | 1.5"-DWS104-CBD 1.5"A-Y | Water | 1.5 | sch 40S | SS | 130 | 105 | DWS | 23 | 13 | 1.5 | A | 8 | 1 | 0 | -8
PS-411 | 2"-DWS104-CBD 1.5"A-Y | Water | 2 | sch 40S | SS | 130 | 105 | DWS | 2 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-411 | 3"-DWS104-CBD 1.5"A-Y | Water | 3 | sch 10S | SS | 130 | 105 | DWS | 2 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-411 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 259 | 13 | 1.5 | A | 39 | 10 | 31 | -8
PS-411 | 6"-DWS104-CBD 1.5"A-Y | Water | 6 | sch 10S | SS | 130 | 105 | DWS | 0 | 13 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 0.5"-DWS103-CBA 1.5"A-Y | Water | 0.5 | SCH 40S | SS | 115 | 105 | DWS | 11 | 7 | 1.5 | A | 2 | 0 | 2 | -8
PS-412 | 0.75"-DWS103-CBA 1.5"A-Y | Water | 0.75 | sch 40S | SS | 115 | 105 | DWS | 1 | 7 | 1.5 | A | 0 | 1 | 0 | -8
PS-412 | 0.75"-DWS104-CBD 1.5"A-Y | Water | 0.75 | sch 40S | SS | 130 | 105 | DWS | 11 | 7 | 1.5 | A | 3 | 0 | 2 | -8
PS-412 | 1"-DWS103-CBA 1.5"A-Y | Water | 1 | sch 40S | SS | 115 | 105 | DWS | 1 | 7 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 1"-DWS104-CBD 1.5"A-Y | Water | 1 | sch 40S | SS | 130 | 105 | DWS | 1 | 7 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 1.5"-DWS104-CBD 1.5"A-Y | Water | 1.5 | sch 40S | SS | 130 | 105 | DWS | 11 | 2 | 1.5 | A | 3 | 2 | 2 | -8
PS-412 | 1.5"-DWS104-CBD 1.5"A-Y | Water | 1.5 | sch 40S | SS | 130 | 105 | DWS | 12 | 3 | 1.5 | A | 4 | 2 | 1 | -8
PS-412 | 1.5"-DWS104-CBD 1.5"A-Y | Water | 1.5 | sch 40S | SS | 130 | 105 | DWS | 13 | 6 | 1.5 | A | 4 | 0 | 2 | -8
PS-412 | 1.5"-DWS104-CBD 1.5"A-Y | Water | 1.5 | sch 40S | SS | 130 | 105 | DWS | 12 | 7 | 1.5 | A | 5 | 0 | 2 | -8
PS-412 | 2"-DWS103-CBA 1.5"A-Y | Water | 2 | sch 40S | SS | 115 | 105 | DWS | 0 | 7 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 2"-DWS104-CBD 1.5"A-Y | Water | 2 | sch 40S | SS | 130 | 105 | DWS | 1 | 2 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 2"-DWS104-CBD 1.5"A-Y | Water | 2 | sch 40S | SS | 130 | 105 | DWS | 2 | 3 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 2"-DWS104-CBD 1.5"A-Y | Water | 2 | sch 40S | SS | 130 | 105 | DWS | 0 | 6 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 2"-DWS104-CBD 1.5"A-Y | Water | 2 | sch 40S | SS | 130 | 105 | DWS | 14 | 7 | 1.5 | A | 2 | 0 | 3 | -8
PS-412 | 3"-DWS104-CBD 1.5"A-Y | Water | 3 | sch 10S | SS | 130 | 105 | DWS | 2 | 2 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 3"-DWS104-CBD 1.5"A-Y | Water | 3 | sch 10S | SS | 130 | 105 | DWS | 1 | 3 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 4"-DWS103-CBA 1.5"A-Y | Water | 4 | sch 10S | SS | 115 | 105 | DWS | 0 | 7 | 1.5 | A | 0 | 0 | 0 | -8
PS-412 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 26 | 2 | 1.5 | A | 2 | 0 | 3 | -8
PS-412 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 24 | 3 | 1.5 | A | 2 | 0 | 3 | -8
PS-412 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 29 | 6 | 1.5 | A | 2 | 1 | 3 | -8
PS-412 | 4"-DWS104-CBD 1.5"A-Y | Water | 4 | sch 10S | SS | 130 | 105 | DWS | 37 | 7 | 1.5 | A | 3 | 1 | 4 | -8
PS520 | 0.5"-CCF1000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 14 | 11 | 1 | A | 5 | 0 | 2 | -8
PS520 | 0.5"-CCF1000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 14 | 12 | 1 | A | 5 | 0 | 2 | -8
PS520 | 0.5"-CCF2000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 31 | 11 | 1 | A | 7 | 0 | 7 | -8
PS520 | 0.5"-CCF2000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 31 | 12 | 1 | A | 7 | 0 | 7 | -8
PS520 | 0.5"-CCF3000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 16 | 11 | 1 | A | 4 | 0 | 3 | -8
PS520 | 0.5"-CCF3000-CBE 1"A-Y | Water | 0.5 | sch 40S | SS | 130 | 120 | CCF | 16 | 12 | 1 | A | 4 | 0 | 3 | -8
PS520 | 2"-CCF1000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 3 | 11 | 1 | A | 0 | 0 | 1 | -8
PS520 | 2"-CCF1000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 3 | 12 | 1 | A | 0 | 0 | 1 | -8
PS520 | 2"-CCF2000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 4 | 11 | 1 | A | 1 | 0 | 1 | -8
PS520 | 2"-CCF2000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 4 | 12 | 1 | A | 1 | 0 | 1 | -8
PS520 | 2"-CCF3000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 3 | 11 | 1 | A | 0 | 0 | 1 | -8
PS520 | 2"-CCF3000-CBE 1"A-Y | Water | 2 | sch 40S | SS | 130 | 120 | CCF | 3 | 12 | 1 | A | 0 | 0 | 1 | -8
PS520 | 2"-CCF4000-CBA 1"A-Y | Water | 2 | sch 40S | SS | 115 | 120 | CCF | 10 | 11 | 1 | A | 2 | 2 | 2 | -8
PS520 | 2"-CCF4000-CBA 1"A-Y | Water | 2 | sch 40S | SS | 115 | 120 | CCF | 10 | 12 | 1 | A | 2 | 2 | 2 | -8
PS-530 | 0.5"-TCF03-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 20 | 14 | 1 | C | 3 | 1 | 8 | -8
PS-530 | 0.5"-TCF04-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 28 | 14 | 1 | C | 5 | 0 | 7 | -8
PS-530 | 0.5"-TCF05-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 18 | 14 | 1 | C | 3 | 1 | 7 | -8
PS-530 | 0.5"-TCF06-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 33 | 14 | 1 | C | 7 | 0 | 10 | -8
PS-530 | 0.5"-TCF30-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 1 | 14 | 1 | C | 1 | 0 | 0 | -8
PS-530 | 0.5"-TCF34-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 136 | 14 | 1 | C | 7 | 0 | 21 | -8
PS-530 | 0.5"-TCF35-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 342 | 14 | 1 | C | 11 | 0 | 49 | -8
PS-530 | 1"-TCF03-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-530 | 1"-TCF05-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-530 | 2"-TCF01-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 5 | 14 | 1 | C | 0 | 2 | 2 | -8
PS-531 | 0.5"-TCF09-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 11 | 14 | 1 | C | 6 | 0 | 4 | -8
PS-531 | 0.5"-TCF10-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 8 | 14 | 1 | C | 3 | 2 | 4 | -8
PS-531 | 0.5"-TCF11-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 8 | 14 | 1 | C | 4 | 2 | 3 | -8
PS-531 | 0.5"-TCF12-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 18 | 14 | 1 | C | 7 | 0 | 5 | -8
PS-531 | 0.5"-TCF28-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 161 | 14 | 1 | C | 8 | 0 | 29 | -8
PS-531 | 0.5"-TCF29-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 381 | 14 | 1 | C | 15 | 0 | 57 | -8
PS-531 | 2"-TCF07-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 4 | 14 | 1 | C | 0 | 3 | 1 | -8
PS-531 | 2"-TCF08-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 2 | 14 | 1 | C | 0 | 2 | 0 | -8
PS-531 | 2"-TCF10-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-531 | 2"-TCF11-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-531 | 2"-TCF13-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 2 | 14 | 1 | C | 0 | 2 | 0 | -8
PS-532 | 0.5"-TCF15-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 8 | 14 | 1 | C | 5 | 1 | 2 | -8
PS-532 | 0.5"-TCF16-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 18 | 14 | 1 | C | 5 | 0 | 3 | -8
PS-532 | 0.5"-TCF18-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 18 | 14 | 1 | C | 6 | 0 | 3 | -8
PS-532 | 0.5"-TCF30-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 225 | 14 | 1 | C | 12 | 2 | 37 | -8
PS-532 | 0.5"-TCF31-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 366 | 14 | 1 | C | 15 | 0 | 54 | -8
PS-532 | 1"-TCF15-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-532 | 1"-TCF16-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-532 | 1"-TCF18-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-532 | 2"-TCF14-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 4 | 14 | 1 | C | 0 | 2 | 1 | -8
PS-532 | 2"-TCF20-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 2 | 14 | 1 | C | 0 | 2 | 0 | -8
PS-533 | 0.5"-TCF22-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 8 | 14 | 1 | C | 5 | 1 | 3 | -8
PS-533 | 0.5"-TCF23-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 18 | 14 | 1 | C | 5 | 0 | 4 | -8
PS-533 | 0.5"-TCF24-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 9 | 14 | 1 | C | 5 | 1 | 3 | -8
PS-533 | 0.5"-TCF25-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 17 | 14 | 1 | C | 5 | 0 | 4 | -8
PS-533 | 0.5"-TCF32-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 136 | 14 | 1 | C | 8 | 0 | 22 | -8
PS-533 | 0.5"-TCF33-GBE 1"C-Y | Water | 0.5 | sch 80 | CPVC | 130 | 120 | TCF | 433 | 14 | 1 | C | 21 | 2 | 65 | -8
PS-533 | 1"-TCF22-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-533 | 1"-TCF23-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-533 | 1"-TCF24-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-533 | 1"-TCF25-GBE 1"C-Y | Water | 1 | sch 80 | CPVC | 130 | 120 | TCF | 0 | 14 | 1 | C | 0 | 0 | 0 | -8
PS-533 | 2"-TCF21-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 4 | 14 | 1 | C | 0 | 2 | 1 | -8
PS-533 | 2"-TCF26-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 3 | 14 | 1 | C | 1 | 1 | 0 | -8
PS-533 | 2"-TCF27-GBE 1"C-Y | Water | 2 | sch 80 | CPVC | 130 | 120 | TCF | 2 | 14 | 1 | C | 0 | 2 | 0 | -8
PS-562A | 1"-FOL03-ABA 1.5"C-Y |  | 1 | sch 80 | CS | 750 |  | FOL | 9 | 13 | 1.5 | C | 4 | 2 | 0 | -8
PS-562A | 2"-FOL03-ABA 1.5"C-Y |  | 2 | sch 80 | CS | 750 |  | FOL | 1 | 13 | 1.5 | C | 0 | 1 | 0 | -8
PS-562A | 3"-FOL02-ABA 1.5"C-Y |  | 3 | sch 40 | CS | 750 |  | FOL | 1 | 13 | 1.5 | C | 0 | 0 | 0 | -8
PS-562A | 3"-FOL03-ABA 1.5"C-Y |  | 3 | sch 40 | CS | 750 |  | FOL | 14 | 13 | 1.5 | C | 2 | 3 | 0 | -8
PS-562A | 4"-FOL01-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 0 | 13 | 1.5 | C | 0 | 0 | 0 | -8
PS-562A | 4"-FOL02-ABA 1.5"C-Y |  | 4 | sch 40 | CS | 750 |  | FOL | 14 | 13 | 1.5 | C | 2 | 2 | 0 | -8
PS-562A | 4"-FOL03-ABA 1.5"C-Y |  | 4 | sch 40 | CS | 750 |  | FOL | 80 | 13 | 1.5 | C | 9 | 5 | 7 | -8
PS-562A | 6"-FOL01-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 64 | 13 | 1.5 | C | 4 | 3 | 6 | -8
PS-562A | 6"-FOL02A-ABA 1.5"C-Y |  | 6 | sch 40 | CS | 750 |  | FOL | 51 | 13 | 1.5 | C | 8 | 1 | 5 | -8
PS-562A | 6"-FOL02-ABA 1.5"C-Y |  | 6 | sch 40 | CS | 750 |  | FOL | 54 | 13 | 1.5 | C | 7 | 6 | 3 | -8
PS-562A | 6"-FOL16-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 9 | 13 | 1.5 | C | 2 | 2 | 1 | -8
PS-562B | 0.75"-FOL17-ABB 1.5"C-Y |  | 0.75 | sch 80 | CS | 225 |  | FOL | 1 | 3 | 1.5 | C | 1 | 0 | 0 | -8
PS-562B | 0.75"-FOL18-ABB 1.5"C-Y |  | 0.75 | sch 80 | CS | 225 |  | FOL | 1 | 3 | 1.5 | C | 1 | 0 | 0 | -8
PS-562B | 0.75"-FOL20-ABB 1.5"C-Y |  | 0.75 | sch 80 | CS | 225 |  | FOL | 1 | 2 | 1.5 | C | 1 | 0 | 0 | -8
PS-562B | 0.75"-FOL21-ABB 1.5"C-Y |  | 0.75 | sch 80 | CS | 225 |  | FOL | 1 | 2 | 1.5 | C | 1 | 0 | 0 | -8
PS-562B | 1"-FOL17-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 3 | 3 | 1.5 | C | 0 | 1 | 0 | -8
PS-562B | 1"-FOL18-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 3 | 3 | 1.5 | C | 0 | 1 | 0 | -8
PS-562B | 1"-FOL20-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 3 | 2 | 1.5 | C | 0 | 1 | 0 | -8
PS-562B | 1"-FOL21-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 3 | 2 | 1.5 | C | 0 | 1 | 0 | -8
PS-562B | 2"-FOL17-ABB 1.5"C-Y |  | 2 | sch 80 | CS | 225 |  | FOL | 0 | 3 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 2"-FOL18-ABB 1.5"C-Y |  | 2 | sch 80 | CS | 225 |  | FOL | 0 | 3 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 2"-FOL21-ABB 1.5"C-Y |  | 2 | sch 80 | CS | 225 |  | FOL | 0 | 2 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 2"-FOL22-ABB 1.5"C-Y |  | 2 | sch 80 | CS | 225 |  | FOL | 0 | 2 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 3"-FOL17-ABB 1.5"C-Y |  | 3 | sch 40 | CS | 225 |  | FOL | 2 | 3 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 3"-FOL18-ABB 1.5"C-Y |  | 3 | sch 40 | CS | 225 |  | FOL | 2 | 3 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 3"-FOL20-ABB 1.5"C-Y |  | 3 | sch 40 | CS | 225 |  | FOL | 2 | 2 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 3"-FOL21-ABB 1.5"C-Y |  | 3 | sch 40 | CS | 225 |  | FOL | 2 | 2 | 1.5 | C | 0 | 0 | 0 | -8
PS-562B | 4"-FOL17-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 10 | 3 | 1.5 | C | 3 | 2 | 2 | -8
PS-562B | 4"-FOL18-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 9 | 3 | 1.5 | C | 2 | 1 | 1 | -8
PS-562B | 4"-FOL20-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 10 | 2 | 1.5 | C | 3 | 2 | 2 | -8
PS-562B | 4"-FOL21-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 9 | 2 | 1.5 | C | 2 | 1 | 1 | -8
PS-562B | 6"-FOL16-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 20 | 13 | 1.5 | C | 2 | 0 | 1 | -8
PS-562B | 6"-FOL18-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 3 | 3 | 1.5 | C | 1 | 0 | 1 | -8
PS-562B | 6"-FOL21-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 3 | 2 | 1.5 | C | 1 | 0 | 1 | -8
PS-562C | 1"-FOL04-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 2 | 13 | 1.5 | C | 0 | 1 | 0 | -8
PS-562C | 1"-FOL05-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 1 | 13 | 1.5 | C | 0 | 0 | 0 | -8
PS-562C | 1"-FOL09-ABB 1.5"C-Y |  | 1 | sch 80 | CS | 225 |  | FOL | 4 | 13 | 1.5 | C | 2 | 2 | 0 | -8
PS-562C | 3"-FOL05-ABB 1.5"C-Y |  | 3 | sch 40 | CS | 225 |  | FOL | 0 | 13 | 1.5 | C | 0 | 0 | 0 | -8
PS-562C | 4"-FOL04-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 0 | 13 | 1.5 | C | 0 | 0 | 0 | -8
PS-562C | 4"-FOL05-ABB 1.5"C-Y |  | 4 | sch 40 | CS | 225 |  | FOL | 93 | 13 | 1.5 | C | 10 | 3 | 9 | -8
PS-562C | 6"-FOL04-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 20 | 13 | 1.5 | C | 3 | 1 | 3 | -8
PS-562C | 6"-FOL09-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 120 | 13 | 1.5 | C | 13 | 7 | 9 | -8
PS-562C | 6"-FOL11-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 33 | 13 | 1.5 | C | 1 | 2 | 3 | -8
PS-562C | 6"-FOL13-ABB 1.5"C-Y |  | 6 | sch 40 | CS | 225 |  | FOL | 33 | 13 | 1.5 | C | 1 | 2 | 2 | -8
PS-562C | 8"-FOL08-ABB 1.5"C-Y |  | 8 | sch 40 | CS | 225 |  | FOL | 94 | 13 | 1.5 | C | 12 | 5 | 8 | -8
PS-562C | 8"-FOL10-ABB 1.5"C-Y |  | 8 | sch 40 | CS | 225 |  | FOL | 33 | 13 | 1.5 | C | 1 | 2 | 3 | -8
PS-562C | 8"-FOL12-ABB 1.5"C-Y |  | 8 | sch 40 | CS | 225 |  | FOL | 33 | 13 | 1.5 | C | 1 | 2 | 2 | -8
PS-960 | 4"-WDR01-ABA 1"B-Y | Water | 4 | sch 40 | CS | 750 | 140 | WDR | 12 | 12 | 1 | B | 3 | 2 | 1 | -8
PS-960 | 6"-WDR01-ABA 1"B-Y | Water | 6 | sch 40 | CS | 750 | 140 | WDR | 10 | 12 | 1 | B | 2 | 1 | 1 | -8
PS-961 | 4"-WDR03-ABA 1"B-Y | Water | 4 | sch 40 | CS | 750 | 140 | WDR | 12 | 11 | 1 | B | 3 | 2 | 1 | -8
PS-961 | 6"-WDR03-ABA 1"B-Y | Water | 6 | sch 40 | CS | 750 | 140 | WDR | 10 | 11 | 1 | B | 2 | 1 | 1 | -8
|  | Water | 2 | sch 40S | SS | 115 | 105 | DWS | 2 | 6 | 1 | B | 0 | 0 | 0 | -8
|  | Water | 2 | SDR11 | HDPE | 120 | 105 | DWS | 7 | 1E | 1 | B | 0 | 0 | 0 | -8
|  | Water | 0.75 | sch 40S | SS | 115 | 105 | DWS | 2 | 7 | 1 | B | 1 | 1 | 0 | -8
|  | Water | 2 | sch 40S | SS | 115 | 105 | DWS | 2 | 7 | 1 | B | 0 | 0 | 0 | -8
|  | Water | 6 | sch 10S | SS | 115 | 105 | DWS | 7 | 8 | 1 | B | 1 | 0 | 0 | -8
|  | Water | 6 | SDR11 | HDPE | 120 | 105 | DWS | 6 | 1A | 1 | B | 0 | 0 | 0 | -8
|  | Water | 6 | sch 10S | SS | 115 | 105 | DWS | 7 | 8 | 1 | B | 1 | 0 | 0 | -8
|  | Water | 6 | SDR11 | HDPE | 120 | 105 | DWS | 6 | 1B | 1 | B | 0 | 0 | 0 | -8
|  | Water | 3 | sch 40 | CS | 750 | 130 | SDR | 27 | 10 | 1 | B | 2 | 0 | 0 | -8
|  | Water | 4 | sch 40 | CS | 750 | 130 | SDR | 34 | 10 | 1 | B | 4 | 0 | 0 | -8
|  | Water | 8 | sch 40 | CS | 750 | 130 | SDR | 32 | 10 | 1 | B | 2 | 3 | 0 | -8
|  | Water | 8 | sch 40 | CS | 750 | 140 | PDR | 8 | 10 | 1 | B | 1 | 1 | 0 | -8
|  | Water | 4 | sch 10S | SS | 115 | 115 | DWT | 4 | 10 | 1 | B | 1 | 1 | 0 | -8

## Heat Loss Data (hidden)
Insulation Thickness | °F | °C | Pipe Diameter | Heat Loss | KED Spec | Preformed Pipe Insulation | Insulation Factor | k Factor @ 50 Deg F
0.5 | 50 | 28 | 0.25 | 1.9 | A | Calcium silicate (ASTM C533) | 1.5 | 0.37
0.5 | 50 | 28 | 0.5 | 2.5 | B | Mineral fiber blanket (ASTM C553) | 1.2 | 0.3
0.5 | 50 | 28 | 0.75 | 2.9 | C | Calcium silicate (ASTM C533) | 1.5 | 0.37
0.5 | 50 | 28 | 1 | 3.5 | D | Mineral fiber blanket (ASTM C553) | 1.2 | 0.3
0.5 | 50 | 28 | 1.25 | 4.1 | E | N/A | 0 | 0
0.5 | 50 | 28 | 1.5 | 4.6
0.5 | 50 | 28 | 2 | 5.5
0.5 | 50 | 28 | 2.5 | 6.5
0.5 | 50 | 28 | 3 | 7.7
0.5 | 50 | 28 | 3.5 | 8.6
0.5 | 50 | 28 | 4 | 9.6
0.5 | 50 | 28 | 6 | 13.6
0.5 | 50 | 28 | 8 | 17.4
0.5 | 50 | 28 | 10 | 21.4
0.5 | 50 | 28 | 12 | 25.2
0.5 | 50 | 28 | 14 | 27.5
0.5 | 50 | 28 | 16 | 31.3
0.5 | 50 | 28 | 18 | 35
0.5 | 50 | 28 | 20 | 38.8
0.5 | 50 | 28 | 24 | 46.2
0.5 | 100 | 56 | 0.25 | 3.9
0.5 | 100 | 56 | 0.5 | 5.2
0.5 | 100 | 56 | 0.75 | 6.1
0.5 | 100 | 56 | 1 | 7.2
0.5 | 100 | 56 | 1.25 | 8.6
0.5 | 100 | 56 | 1.5 | 9.6
0.5 | 100 | 56 | 2 | 11.5
0.5 | 100 | 56 | 2.5 | 13.5
0.5 | 100 | 56 | 3 | 16
0.5 | 100 | 56 | 3.5 | 18
0.5 | 100 | 56 | 4 | 20
0.5 | 100 | 56 | 6 | 28.4
0.5 | 100 | 56 | 8 | 36.3
0.5 | 100 | 56 | 10 | 44.6
0.5 | 100 | 56 | 12 | 52.5
0.5 | 100 | 56 | 14 | 57.4
0.5 | 100 | 56 | 16 | 65.2
0.5 | 100 | 56 | 18 | 73
0.5 | 100 | 56 | 20 | 80.8
0.5 | 100 | 56 | 24 | 96.3
0.5 | 150 | 83 | 0.25 | 6.1
0.5 | 150 | 83 | 0.5 | 8.1
0.5 | 150 | 83 | 0.75 | 9.5
0.5 | 150 | 83 | 1 | 11.2
0.5 | 150 | 83 | 1.25 | 13.4
0.5 | 150 | 83 | 1.5 | 14.9
0.5 | 150 | 83 | 2 | 17.9
0.5 | 150 | 83 | 2.5 | 21.1
0.5 | 150 | 83 | 3 | 25
0.5 | 150 | 83 | 3.5 | 28.1
0.5 | 150 | 83 | 4 | 31.2
0.5 | 150 | 83 | 6 | 44.3
0.5 | 150 | 83 | 8 | 56.6
0.5 | 150 | 83 | 10 | 69.9
0.5 | 150 | 83 | 12 | 81.9
0.5 | 150 | 83 | 14 | 89.5
0.5 | 150 | 83 | 16 | 101.7
0.5 | 150 | 83 | 18 | 113.8
0.5 | 150 | 83 | 20 | 126
0.5 | 150 | 83 | 24 | 150.2
0.5 | 200 | 111 | 0.25 | 8.5
0.5 | 200 | 111 | 0.5 | 11.3
0.5 | 200 | 111 | 0.75 | 13.2
0.5 | 200 | 111 | 1 | 15.6
0.5 | 200 | 111 | 1.25 | 18.6
0.5 | 200 | 111 | 1.5 | 20.7
0.5 | 200 | 111 | 2 | 24.9
0.5 | 200 | 111 | 2.5 | 29.2
0.5 | 200 | 111 | 3 | 34.6
0.5 | 200 | 111 | 3.5 | 39
0.5 | 200 | 111 | 4 | 43.3
0.5 | 200 | 111 | 6 | 61.5
0.5 | 200 | 111 | 8 | 78.6
0.5 | 200 | 111 | 10 | 96.6
0.5 | 200 | 111 | 12 | 113.6
0.5 | 200 | 111 | 14 | 124.2
0.5 | 200 | 111 | 16 | 141.1
0.5 | 200 | 111 | 18 | 158
0.5 | 200 | 111 | 20 | 174.8
0.5 | 200 | 111 | 24 | 208.5
1 | 50 | 28 | 0.25 | 1.3
1 | 50 | 28 | 0.5 | 1.6
1 | 50 | 28 | 0.75 | 1.9
1 | 50 | 28 | 1 | 2.2
1 | 50 | 28 | 1.25 | 2.5
1 | 50 | 28 | 1.5 | 2.8
1 | 50 | 28 | 2 | 3.2
1 | 50 | 28 | 2.5 | 3.8
1 | 50 | 28 | 3 | 4.4
1 | 50 | 28 | 3.5 | 4.9
1 | 50 | 28 | 4 | 5.4
1 | 50 | 28 | 6 | 7.5
1 | 50 | 28 | 8 | 9.4
1 | 50 | 28 | 10 | 11.5
1 | 50 | 28 | 12 | 13.5
1 | 50 | 28 | 14 | 14.7
1 | 50 | 28 | 16 | 16.6
1 | 50 | 28 | 18 | 18.6
1 | 50 | 28 | 20 | 20.5
1 | 50 | 28 | 24 | 24.4
1 | 100 | 56 | 0.25 | 2.7
1 | 100 | 56 | 0.5 | 3.4
1 | 100 | 56 | 0.75 | 3.9
1 | 100 | 56 | 1 | 4.5
1 | 100 | 56 | 1.25 | 5.2
1 | 100 | 56 | 1.5 | 5.8
1 | 100 | 56 | 2 | 6.8
1 | 100 | 56 | 2.5 | 7.8
1 | 100 | 56 | 3 | 9.1
1 | 100 | 56 | 3.5 | 10.2
1 | 100 | 56 | 4 | 11.2
1 | 100 | 56 | 6 | 15.6
1 | 100 | 56 | 8 | 19.7
1 | 100 | 56 | 10 | 24
1 | 100 | 56 | 12 | 28.1
1 | 100 | 56 | 14 | 30.6
1 | 100 | 56 | 16 | 34.7
1 | 100 | 56 | 18 | 38.7
1 | 100 | 56 | 20 | 42.8
1 | 100 | 56 | 24 | 50.9
1 | 150 | 83 | 0.25 | 4.2
1 | 150 | 83 | 0.5 | 5.3
1 | 150 | 83 | 0.75 | 6.1
1 | 150 | 83 | 1 | 7
1 | 150 | 83 | 1.25 | 8.2
1 | 150 | 83 | 1.5 | 9
1 | 150 | 83 | 2 | 10.6
1 | 150 | 83 | 2.5 | 12.2
1 | 150 | 83 | 3 | 14.2
1 | 150 | 83 | 3.5 | 15.9
1 | 150 | 83 | 4 | 17.5
1 | 150 | 83 | 6 | 24.3
1 | 150 | 83 | 8 | 30.7
1 | 150 | 83 | 10 | 37.4
1 | 150 | 83 | 12 | 43.8
1 | 150 | 83 | 14 | 47.8
1 | 150 | 83 | 16 | 54.1
1 | 150 | 83 | 18 | 60.4
1 | 150 | 83 | 20 | 66.7
1 | 150 | 83 | 24 | 79.4
1 | 200 | 111 | 0.25 | 5.8
1 | 200 | 111 | 0.5 | 7.4
1 | 200 | 111 | 0.75 | 8.4
1 | 200 | 111 | 1 | 9.7
1 | 200 | 111 | 1.25 | 11.3
1 | 200 | 111 | 1.5 | 12.4
1 | 200 | 111 | 2 | 14.6
1 | 200 | 111 | 2.5 | 16.9
1 | 200 | 111 | 3 | 19.7
1 | 200 | 111 | 3.5 | 22
1 | 200 | 111 | 4 | 24.2
1 | 200 | 111 | 6 | 33.7
1 | 200 | 111 | 8 | 42.5
1 | 200 | 111 | 10 | 51.9
1 | 200 | 111 | 12 | 60.7
1 | 200 | 111 | 14 | 66.2
1 | 200 | 111 | 16 | 75
1 | 200 | 111 | 18 | 83.8
1 | 200 | 111 | 20 | 92.5
1 | 200 | 111 | 24 | 110
1 | 250 | 139 | 0.25 | 7.6
1 | 250 | 139 | 0.5 | 9.7
1 | 250 | 139 | 0.75 | 11
1 | 250 | 139 | 1 | 12.7
1 | 250 | 139 | 1.25 | 14.8
1 | 250 | 139 | 1.5 | 16.3
1 | 250 | 139 | 2 | 19.1
1 | 250 | 139 | 2.5 | 22.1
1 | 250 | 139 | 3 | 25.8
1 | 250 | 139 | 3.5 | 28.7
1 | 250 | 139 | 4 | 31.7
1 | 250 | 139 | 6 | 44
1 | 250 | 139 | 8 | 55.6
1 | 250 | 139 | 10 | 67.9
1 | 250 | 139 | 12 | 79.4
1 | 250 | 139 | 14 | 86.6
1 | 250 | 139 | 16 | 98.1
1 | 250 | 139 | 18 | 109.6
1 | 250 | 139 | 20 | 121
1 | 250 | 139 | 24 | 143.9
1.5 | 50 | 28 | 0.25 | 1.1
1.5 | 50 | 28 | 0.5 | 1.3
1.5 | 50 | 28 | 0.75 | 1.5
1.5 | 50 | 28 | 1 | 1.7
1.5 | 50 | 28 | 1.25 | 1.9
1.5 | 50 | 28 | 1.5 | 2.1
1.5 | 50 | 28 | 2 | 2.4
1.5 | 50 | 28 | 2.5 | 2.8
1.5 | 50 | 28 | 3 | 3.2
1.5 | 50 | 28 | 3.5 | 3.6
1.5 | 50 | 28 | 4 | 3.9
1.5 | 50 | 28 | 6 | 5.3
1.5 | 50 | 28 | 8 | 6.7
1.5 | 50 | 28 | 10 | 8.1
1.5 | 50 | 28 | 12 | 9.4
1.5 | 50 | 28 | 14 | 10.2
1.5 | 50 | 28 | 16 | 11.5
1.5 | 50 | 28 | 18 | 12.9
1.5 | 50 | 28 | 20 | 14.2
1.5 | 50 | 28 | 24 | 16.8
1.5 | 100 | 56 | 0.25 | 2.2
1.5 | 100 | 56 | 0.5 | 2.8
1.5 | 100 | 56 | 0.75 | 3.1
1.5 | 100 | 56 | 1 | 3.5
1.5 | 100 | 56 | 1.25 | 4
1.5 | 100 | 56 | 1.5 | 4.4
1.5 | 100 | 56 | 2 | 5.1
1.5 | 100 | 56 | 2.5 | 5.8
1.5 | 100 | 56 | 3 | 6.7
1.5 | 100 | 56 | 3.5 | 7.4
1.5 | 100 | 56 | 4 | 8.1
1.5 | 100 | 56 | 6 | 11.1
1.5 | 100 | 56 | 8 | 13.9
1.5 | 100 | 56 | 10 | 16.8
1.5 | 100 | 56 | 12 | 19.6
1.5 | 100 | 56 | 14 | 21.3
1.5 | 100 | 56 | 16 | 24
1.5 | 100 | 56 | 18 | 26.8
1.5 | 100 | 56 | 20 | 29.5
1.5 | 100 | 56 | 24 | 35
1.5 | 150 | 83 | 0.25 | 3.5
1.5 | 150 | 83 | 0.5 | 4.3
1.5 | 150 | 83 | 0.75 | 4.8
1.5 | 150 | 83 | 1 | 5.5
1.5 | 150 | 83 | 1.25 | 6.3
1.5 | 150 | 83 | 1.5 | 6.9
1.5 | 150 | 83 | 2 | 8
1.5 | 150 | 83 | 2.5 | 9.1
1.5 | 150 | 83 | 3 | 10.5
1.5 | 150 | 83 | 3.5 | 11.6
1.5 | 150 | 83 | 4 | 12.7
1.5 | 150 | 83 | 6 | 17.3
1.5 | 150 | 83 | 8 | 21.6
1.5 | 150 | 83 | 10 | 26.2
1.5 | 150 | 83 | 12 | 30.5
1.5 | 150 | 83 | 14 | 33.2
1.5 | 150 | 83 | 16 | 37.5
1.5 | 150 | 83 | 18 | 41.8
1.5 | 150 | 83 | 20 | 46.1
1.5 | 150 | 83 | 24 | 54.6
1.5 | 200 | 111 | 0.25 | 4.8
1.5 | 200 | 111 | 0.5 | 5.9
1.5 | 200 | 111 | 0.75 | 6.7
1.5 | 200 | 111 | 1 | 7.6
1.5 | 200 | 111 | 1.25 | 8.7
1.5 | 200 | 111 | 1.5 | 9.5
1.5 | 200 | 111 | 2 | 11
1.5 | 200 | 111 | 2.5 | 12.6
1.5 | 200 | 111 | 3 | 14.5
1.5 | 200 | 111 | 3.5 | 16.1
1.5 | 200 | 111 | 4 | 17.6
1.5 | 200 | 111 | 6 | 24
1.5 | 200 | 111 | 8 | 30
1.5 | 200 | 111 | 10 | 36.3
1.5 | 200 | 111 | 12 | 42.3
1.5 | 200 | 111 | 14 | 46
1.5 | 200 | 111 | 16 | 52
1.5 | 200 | 111 | 18 | 57.9
1.5 | 200 | 111 | 20 | 63.8
1.5 | 200 | 111 | 24 | 75.7
1.5 | 250 | 139 | 0.25 | 6.3
1.5 | 250 | 139 | 0.5 | 7.8
1.5 | 250 | 139 | 0.75 | 8.7
1.5 | 250 | 139 | 1 | 9.9
1.5 | 250 | 139 | 1.25 | 11.4
1.5 | 250 | 139 | 1.5 | 12.4
1.5 | 250 | 139 | 2 | 14.4
1.5 | 250 | 139 | 2.5 | 16.5
1.5 | 250 | 139 | 3 | 19
1.5 | 250 | 139 | 3.5 | 21
1.5 | 250 | 139 | 4 | 23
1.5 | 250 | 139 | 6 | 31.4
1.5 | 250 | 139 | 8 | 39.2
1.5 | 250 | 139 | 10 | 47.5
1.5 | 250 | 139 | 12 | 55.3
1.5 | 250 | 139 | 14 | 60.2
1.5 | 250 | 139 | 16 | 68
1.5 | 250 | 139 | 18 | 75.7
1.5 | 250 | 139 | 20 | 83.5
1.5 | 250 | 139 | 24 | 99
1.5 | 300 | 167 | 0.25 | 7.9
1.5 | 300 | 167 | 0.5 | 9.7
1.5 | 300 | 167 | 0.75 | 11
1.5 | 300 | 167 | 1 | 12.4
1.5 | 300 | 167 | 1.25 | 14.3
1.5 | 300 | 167 | 1.5 | 15.6
1.5 | 300 | 167 | 2 | 18.1
1.5 | 300 | 167 | 2.5 | 20.6
1.5 | 300 | 167 | 3 | 23.8
1.5 | 300 | 167 | 3.5 | 26.3
1.5 | 300 | 167 | 4 | 28.8
1.5 | 300 | 167 | 6 | 39.3
1.5 | 300 | 167 | 8 | 49.2
1.5 | 300 | 167 | 10 | 59.6
1.5 | 300 | 167 | 12 | 69.3
1.5 | 300 | 167 | 14 | 75.4
1.5 | 300 | 167 | 16 | 85.1
1.5 | 300 | 167 | 18 | 94.9
1.5 | 300 | 167 | 20 | 104.6
1.5 | 300 | 167 | 24 | 124
1.5 | 350 | 194 | 0.25 | 9.6
1.5 | 350 | 194 | 0.5 | 11.9
1.5 | 350 | 194 | 0.75 | 13.3
1.5 | 350 | 194 | 1 | 15.1
1.5 | 350 | 194 | 1.25 | 17.4
1.5 | 350 | 194 | 1.5 | 19
1.5 | 350 | 194 | 2 | 22
1.5 | 350 | 194 | 2.5 | 25.1
1.5 | 350 | 194 | 3 | 28.9
1.5 | 350 | 194 | 3.5 | 32
1.5 | 350 | 194 | 4 | 35
1.5 | 350 | 194 | 6 | 47.8
1.5 | 350 | 194 | 8 | 59.8
1.5 | 350 | 194 | 10 | 72.4
1.5 | 350 | 194 | 12 | 84.3
1.5 | 350 | 194 | 14 | 91.7
1.5 | 350 | 194 | 16 | 103.5
1.5 | 350 | 194 | 18 | 115.4
1.5 | 350 | 194 | 20 | 127.2
1.5 | 350 | 194 | 24 | 150.8
2 | 50 | 28 | 0.25 | 0.9
2 | 50 | 28 | 0.5 | 1.1
2 | 50 | 28 | 0.75 | 1.3
2 | 50 | 28 | 1 | 1.4
2 | 50 | 28 | 1.25 | 1.6
2 | 50 | 28 | 1.5 | 1.8
2 | 50 | 28 | 2 | 2
2 | 50 | 28 | 2.5 | 2.3
2 | 50 | 28 | 3 | 2.6
2 | 50 | 28 | 3.5 | 2.9
2 | 50 | 28 | 4 | 3.1
2 | 50 | 28 | 6 | 4.2
2 | 50 | 28 | 8 | 5.2
2 | 50 | 28 | 10 | 6.3
2 | 50 | 28 | 12 | 7.3
2 | 50 | 28 | 14 | 7.9
2 | 50 | 28 | 16 | 8.9
2 | 50 | 28 | 18 | 9.9
2 | 50 | 28 | 20 | 10.9
2 | 50 | 28 | 24 | 12.9
2 | 100 | 56 | 0.25 | 2
2 | 100 | 56 | 0.5 | 2.4
2 | 100 | 56 | 0.75 | 2.7
2 | 100 | 56 | 1 | 3
2 | 100 | 56 | 1.25 | 3.4
2 | 100 | 56 | 1.5 | 3.7
2 | 100 | 56 | 2 | 4.2
2 | 100 | 56 | 2.5 | 4.8
2 | 100 | 56 | 3 | 5.5
2 | 100 | 56 | 3.5 | 6
2 | 100 | 56 | 4 | 6.6
2 | 100 | 56 | 6 | 8.8
2 | 100 | 56 | 8 | 10.9
2 | 100 | 56 | 10 | 13.1
2 | 100 | 56 | 12 | 15.2
2 | 100 | 56 | 14 | 16.5
2 | 100 | 56 | 16 | 18.6
2 | 100 | 56 | 18 | 20.7
2 | 100 | 56 | 20 | 22.8
2 | 100 | 56 | 24 | 26.9
2 | 150 | 83 | 0.25 | 3.1
2 | 150 | 83 | 0.5 | 3.7
2 | 150 | 83 | 0.75 | 4.2
2 | 150 | 83 | 1 | 4.7
2 | 150 | 83 | 1.25 | 5.3
2 | 150 | 83 | 1.5 | 5.8
2 | 150 | 83 | 2 | 6.6
2 | 150 | 83 | 2.5 | 7.5
2 | 150 | 83 | 3 | 8.5
2 | 150 | 83 | 3.5 | 9.4
2 | 150 | 83 | 4 | 10.2
2 | 150 | 83 | 6 | 13.8
2 | 150 | 83 | 8 | 17
2 | 150 | 83 | 10 | 20.5
2 | 150 | 83 | 12 | 23.8
2 | 150 | 83 | 14 | 25.8
2 | 150 | 83 | 16 | 29
2 | 150 | 83 | 18 | 32.3
2 | 150 | 83 | 20 | 35.5
2 | 150 | 83 | 24 | 42
2 | 200 | 111 | 0.25 | 4.3
2 | 200 | 111 | 0.5 | 5.2
2 | 200 | 111 | 0.75 | 5.8
2 | 200 | 111 | 1 | 6.5
2 | 200 | 111 | 1.25 | 7.4
2 | 200 | 111 | 1.5 | 8
2 | 200 | 111 | 2 | 9.2
2 | 200 | 111 | 2.5 | 10.4
2 | 200 | 111 | 3 | 11.8
2 | 200 | 111 | 3.5 | 13
2 | 200 | 111 | 4 | 14.2
2 | 200 | 111 | 6 | 19.1
2 | 200 | 111 | 8 | 23.6
2 | 200 | 111 | 10 | 28.4
2 | 200 | 111 | 12 | 32.9
2 | 200 | 111 | 14 | 35.7
2 | 200 | 111 | 16 | 40.2
2 | 200 | 111 | 18 | 44.7
2 | 200 | 111 | 20 | 49.2
2 | 200 | 111 | 24 | 58.2
2 | 250 | 139 | 0.25 | 5.6
2 | 250 | 139 | 0.5 | 6.8
2 | 250 | 139 | 0.75 | 7.5
2 | 250 | 139 | 1 | 8.5
2 | 250 | 139 | 1.25 | 9.6
2 | 250 | 139 | 1.5 | 10.4
2 | 250 | 139 | 2 | 12
2 | 250 | 139 | 2.5 | 13.5
2 | 250 | 139 | 3 | 15.5
2 | 250 | 139 | 3.5 | 17
2 | 250 | 139 | 4 | 18.5
2 | 250 | 139 | 6 | 24.9
2 | 250 | 139 | 8 | 30.9
2 | 250 | 139 | 10 | 37.2
2 | 250 | 139 | 12 | 43.1
2 | 250 | 139 | 14 | 46.7
2 | 250 | 139 | 16 | 52.6
2 | 250 | 139 | 18 | 58.5
2 | 250 | 139 | 20 | 64.3
2 | 250 | 139 | 24 | 76.1
2 | 300 | 167 | 0.25 | 7
2 | 300 | 167 | 0.5 | 8.5
2 | 300 | 167 | 0.75 | 9.4
2 | 300 | 167 | 1 | 10.6
2 | 300 | 167 | 1.25 | 12.1
2 | 300 | 167 | 1.5 | 13.1
2 | 300 | 167 | 2 | 15
2 | 300 | 167 | 2.5 | 17
2 | 300 | 167 | 3 | 19.4
2 | 300 | 167 | 3.5 | 21.3
2 | 300 | 167 | 4 | 23.2
2 | 300 | 167 | 6 | 31.2
2 | 300 | 167 | 8 | 38.7
2 | 300 | 167 | 10 | 46.6
2 | 300 | 167 | 12 | 54
2 | 300 | 167 | 14 | 58.6
2 | 300 | 167 | 16 | 65.9
2 | 300 | 167 | 18 | 73.3
2 | 300 | 167 | 20 | 80.6
2 | 300 | 167 | 24 | 95.3
2 | 350 | 194 | 0.25 | 8.5
2 | 350 | 194 | 0.5 | 10.3
2 | 350 | 194 | 0.75 | 11.5
2 | 350 | 194 | 1 | 12.9
2 | 350 | 194 | 1.25 | 14.7
2 | 350 | 194 | 1.5 | 15.9
2 | 350 | 194 | 2 | 18.2
2 | 350 | 194 | 2.5 | 20.6
2 | 350 | 194 | 3 | 23.6
2 | 350 | 194 | 3.5 | 25.9
2 | 350 | 194 | 4 | 28.3
2 | 350 | 194 | 6 | 38
2 | 350 | 194 | 8 | 47.1
2 | 350 | 194 | 10 | 56.6
2 | 350 | 194 | 12 | 65.6
2 | 350 | 194 | 14 | 71.2
2 | 350 | 194 | 16 | 80.2
2 | 350 | 194 | 18 | 89.1
2 | 350 | 194 | 20 | 98.1
2 | 350 | 194 | 24 | 115.9
2.5 | 50 | 28 | 0.25 | 0.9
2.5 | 50 | 28 | 0.5 | 1
2.5 | 50 | 28 | 0.75 | 1.2
2.5 | 50 | 28 | 1 | 1.3
2.5 | 50 | 28 | 1.25 | 1.4
2.5 | 50 | 28 | 1.5 | 1.6
2.5 | 50 | 28 | 2 | 1.8
2.5 | 50 | 28 | 2.5 | 2
2.5 | 50 | 28 | 3 | 2.3
2.5 | 50 | 28 | 3.5 | 2.5
2.5 | 50 | 28 | 4 | 2.7
2.5 | 50 | 28 | 6 | 3.6
2.5 | 50 | 28 | 8 | 4.4
2.5 | 50 | 28 | 10 | 5.2
2.5 | 50 | 28 | 12 | 6.1
2.5 | 50 | 28 | 14 | 6.6
2.5 | 50 | 28 | 16 | 7.4
2.5 | 50 | 28 | 18 | 8.2
2.5 | 50 | 28 | 20 | 9
2.5 | 50 | 28 | 24 | 10.6
2.5 | 100 | 56 | 0.25 | 1.8
2.5 | 100 | 56 | 0.5 | 2.2
2.5 | 100 | 56 | 0.75 | 2.4
2.5 | 100 | 56 | 1 | 2.7
2.5 | 100 | 56 | 1.25 | 3
2.5 | 100 | 56 | 1.5 | 3.3
2.5 | 100 | 56 | 2 | 3.7
2.5 | 100 | 56 | 2.5 | 4.2
2.5 | 100 | 56 | 3 | 4.7
2.5 | 100 | 56 | 3.5 | 5.2
2.5 | 100 | 56 | 4 | 5.6
2.5 | 100 | 56 | 6 | 7.4
2.5 | 100 | 56 | 8 | 9.1
2.5 | 100 | 56 | 10 | 10.9
2.5 | 100 | 56 | 12 | 12.6
2.5 | 100 | 56 | 14 | 13.7
2.5 | 100 | 56 | 16 | 15.3
2.5 | 100 | 56 | 18 | 17
2.5 | 100 | 56 | 20 | 18.7
2.5 | 100 | 56 | 24 | 22
2.5 | 150 | 83 | 0.25 | 2.8
2.5 | 150 | 83 | 0.5 | 3.4
2.5 | 150 | 83 | 0.75 | 3.7
2.5 | 150 | 83 | 1 | 4.2
2.5 | 150 | 83 | 1.25 | 4.7
2.5 | 150 | 83 | 1.5 | 5.1
2.5 | 150 | 83 | 2 | 5.8
2.5 | 150 | 83 | 2.5 | 6.5
2.5 | 150 | 83 | 3 | 7.4
2.5 | 150 | 83 | 3.5 | 8.1
2.5 | 150 | 83 | 4 | 8.7
2.5 | 150 | 83 | 6 | 11.6
2.5 | 150 | 83 | 8 | 14.2
2.5 | 150 | 83 | 10 | 17
2.5 | 150 | 83 | 12 | 19.7
2.5 | 150 | 83 | 14 | 21.3
2.5 | 150 | 83 | 16 | 23.9
2.5 | 150 | 83 | 18 | 26.5
2.5 | 150 | 83 | 20 | 29.1
2.5 | 150 | 83 | 24 | 34.3
2.5 | 200 | 111 | 0.25 | 3.9
2.5 | 200 | 111 | 0.5 | 4.7
2.5 | 200 | 111 | 0.75 | 5.2
2.5 | 200 | 111 | 1 | 5.8
2.5 | 200 | 111 | 1.25 | 6.5
2.5 | 200 | 111 | 1.5 | 7
2.5 | 200 | 111 | 2 | 8
2.5 | 200 | 111 | 2.5 | 9
2.5 | 200 | 111 | 3 | 10.2
2.5 | 200 | 111 | 3.5 | 11.2
2.5 | 200 | 111 | 4 | 12.1
2.5 | 200 | 111 | 6 | 16.1
2.5 | 200 | 111 | 8 | 19.7
2.5 | 200 | 111 | 10 | 23.6
2.5 | 200 | 111 | 12 | 27.2
2.5 | 200 | 111 | 14 | 29.5
2.5 | 200 | 111 | 16 | 33.1
2.5 | 200 | 111 | 18 | 36.7
2.5 | 200 | 111 | 20 | 40.3
2.5 | 200 | 111 | 24 | 47.5
2.5 | 250 | 139 | 0.25 | 5.1
2.5 | 250 | 139 | 0.5 | 6.1
2.5 | 250 | 139 | 0.75 | 6.8
2.5 | 250 | 139 | 1 | 7.6
2.5 | 250 | 139 | 1.25 | 8.5
2.5 | 250 | 139 | 1.5 | 9.2
2.5 | 250 | 139 | 2 | 10.5
2.5 | 250 | 139 | 2.5 | 11.7
2.5 | 250 | 139 | 3 | 13.3
2.5 | 250 | 139 | 3.5 | 14.6
2.5 | 250 | 139 | 4 | 15.8
2.5 | 250 | 139 | 6 | 21
2.5 | 250 | 139 | 8 | 25.8
2.5 | 250 | 139 | 10 | 30.9
2.5 | 250 | 139 | 12 | 35.6
2.5 | 250 | 139 | 14 | 38.6
2.5 | 250 | 139 | 16 | 43.3
2.5 | 250 | 139 | 18 | 48
2.5 | 250 | 139 | 20 | 52.8
2.5 | 250 | 139 | 24 | 62.2
2.5 | 300 | 167 | 0.25 | 6.4
2.5 | 300 | 167 | 0.5 | 7.7
2.5 | 300 | 167 | 0.75 | 8.5
2.5 | 300 | 167 | 1 | 9.5
2.5 | 300 | 167 | 1.25 | 10.7
2.5 | 300 | 167 | 1.5 | 11.5
2.5 | 300 | 167 | 2 | 13.1
2.5 | 300 | 167 | 2.5 | 14.7
2.5 | 300 | 167 | 3 | 16.7
2.5 | 300 | 167 | 3.5 | 18.3
2.5 | 300 | 167 | 4 | 19.8
2.5 | 300 | 167 | 6 | 26.3
2.5 | 300 | 167 | 8 | 32.3
2.5 | 300 | 167 | 10 | 38.7
2.5 | 300 | 167 | 12 | 44.6
2.5 | 300 | 167 | 14 | 48.4
2.5 | 300 | 167 | 16 | 54.3
2.5 | 300 | 167 | 18 | 60.2
2.5 | 300 | 167 | 20 | 66.1
2.5 | 300 | 167 | 24 | 77.9
2.5 | 350 | 194 | 0.25 | 7.8
2.5 | 350 | 194 | 0.5 | 9.3
2.5 | 350 | 194 | 0.75 | 10.3
2.5 | 350 | 194 | 1 | 11.5
2.5 | 350 | 194 | 1.25 | 13
2.5 | 350 | 194 | 1.5 | 14
2.5 | 350 | 194 | 2 | 15.9
2.5 | 350 | 194 | 2.5 | 17.9
2.5 | 350 | 194 | 3 | 20.3
2.5 | 350 | 194 | 3.5 | 22.2
2.5 | 350 | 194 | 4 | 24.1
2.5 | 350 | 194 | 6 | 32
2.5 | 350 | 194 | 8 | 39.3
2.5 | 350 | 194 | 10 | 47.1
2.5 | 350 | 194 | 12 | 54.3
2.5 | 350 | 194 | 14 | 58.8
2.5 | 350 | 194 | 16 | 66
2.5 | 350 | 194 | 18 | 73.2
2.5 | 350 | 194 | 20 | 80.4
2.5 | 350 | 194 | 24 | 94.7
3 | 50 | 28 | 0.25 | 0.8
3 | 50 | 28 | 0.5 | 1
3 | 50 | 28 | 0.75 | 1.1
3 | 50 | 28 | 1 | 1.2
3 | 50 | 28 | 1.25 | 1.3
3 | 50 | 28 | 1.5 | 1.4
3 | 50 | 28 | 2 | 1.6
3 | 50 | 28 | 2.5 | 1.8
3 | 50 | 28 | 3 | 2
3 | 50 | 28 | 3.5 | 2.2
3 | 50 | 28 | 4 | 2.4
3 | 50 | 28 | 6 | 3.1
3 | 50 | 28 | 8 | 3.8
3 | 50 | 28 | 10 | 4.5
3 | 50 | 28 | 12 | 5.2
3 | 50 | 28 | 14 | 5.6
3 | 50 | 28 | 16 | 6.3
3 | 50 | 28 | 18 | 7
3 | 50 | 28 | 20 | 7.6
3 | 50 | 28 | 24 | 9
3 | 100 | 56 | 0.25 | 1.7
3 | 100 | 56 | 0.5 | 2
3 | 100 | 56 | 0.75 | 2.2
3 | 100 | 56 | 1 | 2.4
3 | 100 | 56 | 1.25 | 2.7
3 | 100 | 56 | 1.5 | 2.9
3 | 100 | 56 | 2 | 3.3
3 | 100 | 56 | 2.5 | 3.7
3 | 100 | 56 | 3 | 4.2
3 | 100 | 56 | 3.5 | 4.6
3 | 100 | 56 | 4 | 4.9
3 | 100 | 56 | 6 | 6.5
3 | 100 | 56 | 8 | 7.9
3 | 100 | 56 | 10 | 9.4
3 | 100 | 56 | 12 | 10.8
3 | 100 | 56 | 14 | 11.7
3 | 100 | 56 | 16 | 13.1
3 | 100 | 56 | 18 | 14.5
3 | 100 | 56 | 20 | 15.9
3 | 100 | 56 | 24 | 18.7
3 | 150 | 83 | 0.25 | 2.6
3 | 150 | 83 | 0.5 | 3.1
3 | 150 | 83 | 0.75 | 3.4
3 | 150 | 83 | 1 | 3.8
3 | 150 | 83 | 1.25 | 4.3
3 | 150 | 83 | 1.5 | 4.6
3 | 150 | 83 | 2 | 5.2
3 | 150 | 83 | 2.5 | 5.8
3 | 150 | 83 | 3 | 6.6
3 | 150 | 83 | 3.5 | 7.1
3 | 150 | 83 | 4 | 7.7
3 | 150 | 83 | 6 | 10.1
3 | 150 | 83 | 8 | 12.4
3 | 150 | 83 | 10 | 14.7
3 | 150 | 83 | 12 | 16.9
3 | 150 | 83 | 14 | 18.3
3 | 150 | 83 | 16 | 20.5
3 | 150 | 83 | 18 | 22.6
3 | 150 | 83 | 20 | 24.8
3 | 150 | 83 | 24 | 29.2
3 | 200 | 111 | 0.25 | 3.6
3 | 200 | 111 | 0.5 | 4.3
3 | 200 | 111 | 0.75 | 4.8
3 | 200 | 111 | 1 | 5.3
3 | 200 | 111 | 1.25 | 5.9
3 | 200 | 111 | 1.5 | 6.4
3 | 200 | 111 | 2 | 7.2
3 | 200 | 111 | 2.5 | 8
3 | 200 | 111 | 3 | 9.1
3 | 200 | 111 | 3.5 | 9.9
3 | 200 | 111 | 4 | 10.7
3 | 200 | 111 | 6 | 14
3 | 200 | 111 | 8 | 17.1
3 | 200 | 111 | 10 | 20.4
3 | 200 | 111 | 12 | 23.4
3 | 200 | 111 | 14 | 25.3
3 | 200 | 111 | 16 | 28.3
3 | 200 | 111 | 18 | 31.4
3 | 200 | 111 | 20 | 34.4
3 | 200 | 111 | 24 | 40.4
3 | 250 | 139 | 0.25 | 4.8
3 | 250 | 139 | 0.5 | 5.7
3 | 250 | 139 | 0.75 | 6.2
3 | 250 | 139 | 1 | 6.9
3 | 250 | 139 | 1.25 | 7.8
3 | 250 | 139 | 1.5 | 8.3
3 | 250 | 139 | 2 | 9.4
3 | 250 | 139 | 2.5 | 10.5
3 | 250 | 139 | 3 | 11.9
3 | 250 | 139 | 3.5 | 12.9
3 | 250 | 139 | 4 | 14
3 | 250 | 139 | 6 | 18.3
3 | 250 | 139 | 8 | 22.4
3 | 250 | 139 | 10 | 26.6
3 | 250 | 139 | 12 | 30.6
3 | 250 | 139 | 14 | 33.1
3 | 250 | 139 | 16 | 37.1
3 | 250 | 139 | 18 | 41
3 | 250 | 139 | 20 | 45
3 | 250 | 139 | 24 | 52.8
3 | 300 | 167 | 0.25 | 6
3 | 300 | 167 | 0.5 | 7.1
3 | 300 | 167 | 0.75 | 7.8
3 | 300 | 167 | 1 | 8.7
3 | 300 | 167 | 1.25 | 9.7
3 | 300 | 167 | 1.5 | 10.4
3 | 300 | 167 | 2 | 11.8
3 | 300 | 167 | 2.5 | 13.2
3 | 300 | 167 | 3 | 14.9
3 | 300 | 167 | 3.5 | 16.2
3 | 300 | 167 | 4 | 17.5
3 | 300 | 167 | 6 | 23
3 | 300 | 167 | 8 | 28.1
3 | 300 | 167 | 10 | 33.4
3 | 300 | 167 | 12 | 38.4
3 | 300 | 167 | 14 | 41.5
3 | 300 | 167 | 16 | 46.5
3 | 300 | 167 | 18 | 51.4
3 | 300 | 167 | 20 | 56.3
3 | 300 | 167 | 24 | 66.2
3 | 350 | 194 | 0.25 | 7.3
3 | 350 | 194 | 0.5 | 8.6
3 | 350 | 194 | 0.75 | 9.5
3 | 350 | 194 | 1 | 10.5
3 | 350 | 194 | 1.25 | 11.8
3 | 350 | 194 | 1.5 | 12.7
3 | 350 | 194 | 2 | 14.3
3 | 350 | 194 | 2.5 | 16
3 | 350 | 194 | 3 | 18.1
3 | 350 | 194 | 3.5 | 19.7
3 | 350 | 194 | 4 | 21.3
3 | 350 | 194 | 6 | 28
3 | 350 | 194 | 8 | 34.1
3 | 350 | 194 | 10 | 40.6
3 | 350 | 194 | 12 | 46.7
3 | 350 | 194 | 14 | 50.5
3 | 350 | 194 | 16 | 56.5
3 | 350 | 194 | 18 | 62.5
3 | 350 | 194 | 20 | 68.5
3 | 350 | 194 | 24 | 80.5
4 | 50 | 28 | 0.25 | 0.7
4 | 50 | 28 | 0.5 | 0.9
4 | 50 | 28 | 0.75 | 0.9
4 | 50 | 28 | 1 | 1
4 | 50 | 28 | 1.25 | 1.1
4 | 50 | 28 | 1.5 | 1.2
4 | 50 | 28 | 2 | 1.4
4 | 50 | 28 | 2.5 | 1.5
4 | 50 | 28 | 3 | 1.7
4 | 50 | 28 | 3.5 | 1.8
4 | 50 | 28 | 4 | 2
4 | 50 | 28 | 6 | 2.5
4 | 50 | 28 | 8 | 3.1
4 | 50 | 28 | 10 | 3.6
4 | 50 | 28 | 12 | 4.1
4 | 50 | 28 | 14 | 4.4
4 | 50 | 28 | 16 | 5
4 | 50 | 28 | 18 | 5.5
4 | 50 | 28 | 20 | 6
4 | 50 | 28 | 24 | 7
4 | 100 | 56 | 0.25 | 1.5
4 | 100 | 56 | 0.5 | 1.8
4 | 100 | 56 | 0.75 | 2
4 | 100 | 56 | 1 | 2.1
4 | 100 | 56 | 1.25 | 2.4
4 | 100 | 56 | 1.5 | 2.5
4 | 100 | 56 | 2 | 2.9
4 | 100 | 56 | 2.5 | 3.2
4 | 100 | 56 | 3 | 3.5
4 | 100 | 56 | 3.5 | 3.8
4 | 100 | 56 | 4 | 4.1
4 | 100 | 56 | 6 | 5.3
4 | 100 | 56 | 8 | 6.4
4 | 100 | 56 | 10 | 7.5
4 | 100 | 56 | 12 | 8.6
4 | 100 | 56 | 14 | 9.3
4 | 100 | 56 | 16 | 10.3
4 | 100 | 56 | 18 | 11.4
4 | 100 | 56 | 20 | 12.4
4 | 100 | 56 | 24 | 14.5
4 | 150 | 83 | 0.25 | 2.4
4 | 150 | 83 | 0.5 | 2.8
4 | 150 | 83 | 0.75 | 3
4 | 150 | 83 | 1 | 3.4
4 | 150 | 83 | 1.25 | 3.7
4 | 150 | 83 | 1.5 | 4
4 | 150 | 83 | 2 | 4.4
4 | 150 | 83 | 2.5 | 4.9
4 | 150 | 83 | 3 | 5.5
4 | 150 | 83 | 3.5 | 6
4 | 150 | 83 | 4 | 6.4
4 | 150 | 83 | 6 | 8.3
4 | 150 | 83 | 8 | 10
4 | 150 | 83 | 10 | 11.8
4 | 150 | 83 | 12 | 13.4
4 | 150 | 83 | 14 | 14.5
4 | 150 | 83 | 16 | 16.1
4 | 150 | 83 | 18 | 17.8
4 | 150 | 83 | 20 | 19.4
4 | 150 | 83 | 24 | 22.7
4 | 200 | 111 | 0.25 | 3.3
4 | 200 | 111 | 0.5 | 3.9
4 | 200 | 111 | 0.75 | 4.2
4 | 200 | 111 | 1 | 4.6
4 | 200 | 111 | 1.25 | 5.2
4 | 200 | 111 | 1.5 | 5.5
4 | 200 | 111 | 2 | 6.2
4 | 200 | 111 | 2.5 | 6.8
4 | 200 | 111 | 3 | 7.6
4 | 200 | 111 | 3.5 | 8.3
4 | 200 | 111 | 4 | 8.9
4 | 200 | 111 | 6 | 11.4
4 | 200 | 111 | 8 | 13.8
4 | 200 | 111 | 10 | 16.3
4 | 200 | 111 | 12 | 18.6
4 | 200 | 111 | 14 | 20
4 | 200 | 111 | 16 | 22.3
4 | 200 | 111 | 18 | 24.6
4 | 200 | 111 | 20 | 26.9
4 | 200 | 111 | 24 | 31.4
4 | 250 | 139 | 0.25 | 4.3
4 | 250 | 139 | 0.5 | 5.1
4 | 250 | 139 | 0.75 | 5.5
4 | 250 | 139 | 1 | 6.1
4 | 250 | 139 | 1.25 | 6.7
4 | 250 | 139 | 1.5 | 7.2
4 | 250 | 139 | 2 | 8.1
4 | 250 | 139 | 2.5 | 8.9
4 | 250 | 139 | 3 | 10
4 | 250 | 139 | 3.5 | 10.8
4 | 250 | 139 | 4 | 11.6
4 | 250 | 139 | 6 | 15
4 | 250 | 139 | 8 | 18.1
4 | 250 | 139 | 10 | 21.3
4 | 250 | 139 | 12 | 24.3
4 | 250 | 139 | 14 | 26.2
4 | 250 | 139 | 16 | 29.2
4 | 250 | 139 | 18 | 32.2
4 | 250 | 139 | 20 | 35.2
4 | 250 | 139 | 24 | 41.1
4 | 300 | 167 | 0.25 | 5.4
4 | 300 | 167 | 0.5 | 6.3
4 | 300 | 167 | 0.75 | 6.9
4 | 300 | 167 | 1 | 7.6
4 | 300 | 167 | 1.25 | 8.5
4 | 300 | 167 | 1.5 | 9
4 | 300 | 167 | 2 | 10.1
4 | 300 | 167 | 2.5 | 11.2
4 | 300 | 167 | 3 | 12.5
4 | 300 | 167 | 3.5 | 13.5
4 | 300 | 167 | 4 | 14.6
4 | 300 | 167 | 6 | 18.8
4 | 300 | 167 | 8 | 22.6
4 | 300 | 167 | 10 | 26.7
4 | 300 | 167 | 12 | 30.5
4 | 300 | 167 | 14 | 32.8
4 | 300 | 167 | 16 | 36.6
4 | 300 | 167 | 18 | 40.3
4 | 300 | 167 | 20 | 44.1
4 | 300 | 167 | 24 | 51.5
4 | 350 | 194 | 0.25 | 6.6
4 | 350 | 194 | 0.5 | 7.7
4 | 350 | 194 | 0.75 | 8.4
4 | 350 | 194 | 1 | 9.3
4 | 350 | 194 | 1.25 | 10.3
4 | 350 | 194 | 1.5 | 11
4 | 350 | 194 | 2 | 12.3
4 | 350 | 194 | 2.5 | 13.6
4 | 350 | 194 | 3 | 15.2
4 | 350 | 194 | 3.5 | 16.5
4 | 350 | 194 | 4 | 17.7
4 | 350 | 194 | 6 | 22.8
4 | 350 | 194 | 8 | 27.5
4 | 350 | 194 | 10 | 32.4
4 | 350 | 194 | 12 | 37.1
4 | 350 | 194 | 14 | 39.9
4 | 350 | 194 | 16 | 44.5
4 | 350 | 194 | 18 | 49
4 | 350 | 194 | 20 | 53.6
4 | 350 | 194 | 24 | 62.6
This shape represents a table slicer. Table slicers are supported in Excel 2013 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are supported in Excel 2013 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are supported in Excel 2013 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Data Summary (hidden)
Self-Regulating/Power-Limiting Cables | SR Cable Type | UOM | Cable Length (LF) | Mineral-Insulated Cable | MI Cable Type2 | UOM | QTY | Accessories/Circuits | End Seal Kits |  | Power Kits |  | Controllers |  | RTD 1 |  | Electrical Traced Label
| 10BTV1-CT | FT | 563 |  | 32 Series MI | FT | 1057 |  | Description | QTY | Description | QTY | Description | QTY | Description | QTY | Description | QTY (EA)
| 10QTVR1-CT | FT | 125 | [5 empty] | E-100-A | 199 | JBS-100-A | 199 | 910*E1WL*SSR2 | 15 | RTD10CS | 15 | ETL-ENGLISH | 1066
| 10VPL1-CT | FT | 699
| 15QTVR1-CT | FT | 1730 | [5 empty] | Glass Tape |  | Pipe Straps |  | Junction Box |  | RTD 2 |  | Circuits
| 20QTVR-CT | FT | 910 | [5 empty] | Description | QTY (ROLL) | Description | QTY (EA) | Description | QTY | Description | QTY | QTY
| 3BTV1-CT | FT | 3910 | [5 empty] | GT-66 | 793 | PB 1000 | 146 | PTJB | 48 | RTD4AL | 15 | 281
| 5BTV1-CT | FT | 655 | [7 empty] | PB 2400 | 708
| 5VPL1-CT | FT | 3560 | [7 empty] | PB 300 | 22
| 8BTV1-CT | FT | 682 | [7 empty] | PS-03 | 166
[11 empty] | PS-10 | 225
[11 empty] | PS-20 | 16

## Quote Sheet
Project Name:
Pricing Breakdown |  |  | Cat. Number | Qty | Unit | Self Perform |  | Pentair |  | Thermon |  | Chromalax
Description
Heat Trace Materials
[6 empty] | 2 |  | 1 |  | 2 |  | 3
|  | Required | User Input | 361 |  | Unit Rate | Total | Unit Rate | Total | Unit Rate | Total | Unit Rate | Total
1 | Heat Trace Control Panel - 16 circuit | N |  | 0 | EA | 10350 | 0 | 9073.27 | 0 | 10350 | 0 | 9520 | 0
2 | Heat Trace Control Panel - 42 circuit | Y |  | 9 | EA | 18200 | 163800 | 15083.32 | 135749.88 | 18200 | 163800 | 24990 | 224910
3 | Heat Trace Line Sensing Control Panel - 36 circuit | N |  | 0 | EA | 30500 | 0 | 37801.97 | 0 | 30500 | 0 | 28800 | 0
4 | Heat Trace Line Sensing Control Panel - 72 circuit | N |  | 0 | EA | 45000 | 0 | 51389.64 | 0 | 45000 | 0 | 57240 | 0
Heat Trace Control Panels Sub-Total |  |  |  | 9 |  | 18200 | 163800 | 15083.32 | 135749.88 | 18200 | 163800 | 24990 | 224910
1 | Heat Trace Transformer 30 kVA | N |  | 0 | EA | 2500 | 0 | 2267.03 | 0 | 2500 | 0 | 4800 | 0
2 | Heat Trace Transformer 45 kVA | N |  | 0 | EA | 3900 | 0 | 2720.23 | 0 | 3900 | 0 | 5600 | 0
3 | Heat Trace Transformer 75 kVA | Y |  | 9 | EA | 4200 | 37800 | 3870.74 | 34836.66 | 4200 | 37800 | 6200 | 55800
Heat Trace Transformers Sub-Total |  |  |  | 9 |  | 4200 | 37800 | 3870.74 | 34836.66 | 4200 | 37800 | 13.2857 | 55800
1 | 10 W/ft, 120V Self-Reg Heating Cable |  | 10XTV1-CT-T3 | 0 | FT | 6.9 | 0 | 4.35 | 0 | 6.9 | 0 | 2.9 | 0
2 | 5 W/ft, 120V Self-Reg Heating Cable |  | 5XTVR1-CT-T2 | 0 | FT | 6.9 | 0 | 4.33 | 0 | 6.9 | 0 | 2.9 | 0
3 | 15 W/ft, 120V Self-Reg Heating Cable |  | 15XTVR1-CT-T3 | 0 | FT | 6.9 | 0 | 4.44 | 0 | 6.9 | 0 | 2.9 | 0
4 | 10 W/ft, 120V Self-Reg Heating Cable |  | 10BTV1-CT | 563 | FT | 5 | 2815 | 2.98 | 1677.74 | 5 | 2815 | 1.9 | 1069.7
5 | 10 W/ft, 120V Self-Reg Heating Cable |  | 10QTVR1-CT | 125 | FT | 6.9 | 862.5 | 3.41 | 426.25 | 6.9 | 862.5 | 2.4 | 300
6 | 15 W/ft, 120V Self-Reg Heating Cable |  | 15QTVR1-CT | 1730 | FT | 6.9 | 11937 | 4.75 | 8217.5 | 6.9 | 11937 | 2.4 | 4152
7 | 20 W/ft, 120V Self-Reg Heating Cable |  | 20QTVR-CT | 910 | FT | 6.9 | 6279 | 4.5 | 4095 | 6.9 | 6279 | 2.4 | 2184
8 | 3 W/ft, 120V Self-Reg Heating Cable |  | 3BTV1-CT | 3910 | FT | 5 | 19550 | 2.11 | 8250.1 | 5 | 19550 | 1.9 | 7429
9 | 5 W/ft, 120V Self-Reg Heating Cable |  | 5BTV1-CT | 655 | FT | 5 | 3275 | 2.04 | 1336.2 | 5 | 3275 | 1.9 | 1244.5
10 | 8 W/ft, 120V Self-Reg Heating Cable |  | 8BTV1-CT | 682 | FT | 5 | 3410 | 2.82 | 1923.24 | 5 | 3410 | 1.9 | 1295.8
11 | 10 W/ft, 120V Self-Reg Heating Cable |  | 10VPL1-CT | 699 | FT | 9.75 | 6815.25 | 6.98 | 4879.02 | 9.75 | 6815.25 | 5.25 | 3669.75
12 | 15 W/ft, 120V Self-Reg Heating Cable |  | 15VPL1-CT | 0 | FT | 9.75 | 0 | 7.39 | 0 | 9.75 | 0 | 5.25 | 0
13 | 5 W/ft, 120V Self-Reg Heating Cable |  | 5VPL1-CT | 3560 | FT | 9.75 | 34710 | 7.12 | 25347.2 | 9.75 | 34710 | 5.25 | 18690
14 | 20 W/ft, 120V Self-Reg Heating Cable |  | 20VPL1-CT | 0 | FT | 9.75 | 0 | 7 | 0 | 9.75 | 0 | 5.25 | 0
15 | 300V Pyrotenax Dual Conductor MI Heating Cable |  | 32 Series MI | 1057 | FT | 3.5 | 3699.5 | 3.17 | 3350.69 | 3.5 | 3699.5 | 2.95 | 3118.15
16 | 600V Pyrotenax Dual Conductor MI Heating Cable |  | 62 Series MI | 0 | FT | 7 | 0 | 7.35 | 0 | 7 | 0 | 5.95 | 0
HTXR Cable Sub-Total |  |  |  | 13891 |  | 6.7204 | 93353.25 | 4.2836 | 59502.94 | 6.7204 | 93353.25 | 3.1065 | 43152.9
1 | Above-Insulation End Seal Kit |  | E-100-A | 199 | EA | 44.75 | 8905.25 | 52.93 | 10533.07 | 44.75 | 8905.25 | 28.6 | 5691.4
2 | Single Entry Power Kit with J. Box |  | JBS-100-A | 199 | EA | 75 | 14925 | 91.58 | 18224.42 | 75 | 14925 | 123.75 | 24626.25
3 | DigiTrace 910 1pt Controller, 2 pole 30A 277V SSR |  | 910*E1WL*SSR2 | 15 | EA | 2450 | 36750 | 761.39 | 11420.85 | 2450 | 36750 | 775 | 11625
4 | DigiTrace RTD with 10 foot S/S Corrugated Shield |  | RTD10CS | 15 | EA | 225 | 3375 | 113.8 | 1707 | 225 | 3375 | 96.25 | 1443.75
5 | Electrical Traced Label for traced pipes and tanks |  | ETL-ENGLISH | 1066 | EA | 0.25 | 266.5 | 0.64 | 682.24 | 0.25 | 266.5 | 4.55 | 4850.3
6 | Glass Tape (66ft/roll) (Not for Stainless-Steel Pipe) |  | GT-66 | 793 | ROLL | 9 | 7137 | 3.98 | 3156.14 | 9 | 7137 | 7 | 5551
7 | Pipe strap 1-3 in. |  | PS-03 | 166 | EA | 1.8 | 298.8 | 0.19 | 31.54 | 1.8 | 298.8 | 3.95 | 655.7
8 | Pipe strap 3-10 in. |  | PS-10 | 225 | EA | 2.25 | 506.25 | 3.5 | 787.5 | 2.25 | 506.25 | 4.4 | 990
9 | Pipe strap 10-20 in. |  | PS-20 | 16 | EA | 3.1 | 49.6 | 4.89 | 78.24 | 3.1 | 49.6 | 5.5 | 88
10 | Pipe Straps for MI Cables - 1 to 3 in. (package of 35 pc) |  | PB 300 | 22 | BAG | 0.05 | 1.1 | 6.39 | 140.58 | 0.05 | 1.1 | 0 | 0
11 | Pipe Straps for MI Cables - 3 to 6 in. (package of 25 pc) |  | PB 600 | 0 | BAG | 0.05 | 0 | 6.39 | 0 | 0.05 | 1.1 | 0 | 0
12 | Pipe Straps for MI Cables - 8 to 10 in. |  | PB 1000 | 146 | EA | 0.05 | 7.3 | 6.39 | 932.94 | 0.05 | 7.3 | 0 | 0
13 | Pipe Straps for MI Cables - 10 to 12 in. |  | PB 1200 | 0 | EA | 0.05 | 0 | 6.39 | 0 | 0.05 | 0 | 0 | 0
14 | Pipe Straps for MI Cables - 12 in. & above |  | PB 2400 | 708 | EA | 0.05 | 35.4 | 6.39 | 4524.12 | 0.05 | 35.4 | 0 | 0
15 | Ferralloy Junction Box, CID1, 3 Hubs |  | PTJB | 48 | EA | 350 | 16800 | 157.29 | 7549.92 | 350 | 16800 | 297 | 14256
16 | DigiTrace RTD, -100F to 900F, Pipe Mount |  | RTD4AL | 15 | EA | 120 | 1800 | 57.57 | 863.55 | 120 | 1800 | 96.25 | 1443.75
17 | Stainless Steel Tags |  |  | 48 | EA | 8.5 | 408 | 2.74 | 131.52 | 8.5 | 408 | 7.5 | 360
Heat Trace Accessories Sub-Total |  |  |  | 1 | PLS | 91265.2 | 91265.2 | 60763.63 | 60763.63 | 91266.3 | 91266.3 | 71581.15 | 71581.15
Heat Trace (Self Regulating Cable, MI Cable. Accessories Included) Sub-Total |  |  |  | 13891 | LF | 13.2905 | 184618.45 | 8.6579 | 120266.57 | 13.2906 | 184619.55 | 8.2596 | 114734.05
Vendor Pipe Sub-Total |  |  |  | 10708 | LF | 13.2905 | 142314.7623
Heat Trace Sub-Total |  |  |  | 1 | PLS | 528533.2123 | 528533.2123 | 290853.11 | 290853.11 | 386219.55 | 386219.55 | 395444.05 | 395444.05
Electrical Materials
|  | QTY per Circuit | Size | QTY | UOM | 2 |  | 1 |  | 2 |  | 3
1 | Conduit (LF) | 20 | 3/4" RGS | 7220 | LF | 5.97 | 43103.4 | 5.96 | 43031.2 | 5.97 | 43103.4 | 5.96 | 43031.2
2 | Wire (LF) | 100 | 3/c-10 | 36400 | LF | 0.91 | 33124 | 1.48 | 53872 | 0.91 | 33124 | 1.48 | 53872
3 | RTD Wire (LF) | 100 | 1 pr 16 KX | 3000 | LF | 1 | 3000 | 1 | 3000 | 1 | 3000 | 1 | 3000
4 | Terminations (EA) | 6 | N/A | 2346 | EA | 2.01 | 4715.46 | 1.94 | 4551.24 | 2.01 | 4715.46 | 1.94 | 4551.24
| Electrical Materials Sub-Total | [5 empty] | 83942.86 |  | 104454.44 |  | 83942.86 |  | 104454.44
Total | 612476.0723

## SUB QCS (hidden)
QUOTE COMPARISON SHEET - SUBCONTRACT
Primary DOR: Technical Staff pink sections, Procurement Staff everything else. | [5 empty] | Status: |  |  | Need Awarding | Not on AVL |  | Not Qualified | Supplier On AVL |  | Need Awarding |  |  | Carried |  |  | Need Awarding
872 - Heat Tracing | [5 empty] | BID DUE: | Use this column when a combination of |  |  | 2015-11-13 |  |  | 2015-11-13
[6 empty] | RFP SENT: | selections from more than one bid is |  |  | 2015-11-04 |  |  | 2015-11-04
[6 empty] | BID DURATION: | necessary or yields the best option. |  |  |  | 9 | Days |  | 9 | Days |  | 0 | Days |  | 0 | Days
| Project No.: | 20007470 |  |  |  |  | COMBINED SELECTION |  |  | BIDDER 1 |  |  | BIDDER 2 |  |  | BIDDER 3 |  |  | BIDDER X
| Project Name: | 0 |  |  |  | Bidder Legal Name: |  |  |  | Thermon Heat Tracing Services-I, Inc. |  |  | Chromalox Inc |  |  | Kiewit Self-Perform |  |  | (Keep BIDDER X columns blank)
| Owner: | Advanced Power |  |  |  | Bidder Contact Name: |  |  |  | Clint Tyler |  |  | Larry Kapalin | [5 empty] | (To add another bidder, copy BIDDER X
| Job Site: |  |  |  |  | Bidder Contact Email: |  |  |  | clint.tyler@thermon.com |  |  | larry.kapalin@chromalox.com | [5 empty] | and insert in front of at least one Bidder
| RFP Description: | Heat Tracing |  |  |  | Bidder Phone: |  |  |  | 713-799-4300 |  |  | 815-355-5863 | [5 empty] | before BIDDER X)
| Spec: | 872 |  |  |  | Bid Date or "No Bid": |  |  |  | 2015-11-12 |  |  | 2015-11-13
| HD Quote Group Tag: | 7.26 |  |  |  | Bid Valid Until Date: |  |  |  | 2016-02-11 |  |  | 2016-02-11
| Engineering: | Eric Fohrenck |  |  |  | Bid Validity Duration (Days): |  |  |  | 91 |  |  | 90
| Procurement: | Grant Bunch |  |  |  | Firm or Budgetary Bid: |  |  |  | Budgetary Bid |  |  | Budgetary Bid
| Reviewer: | Brian Roser |  |  |  | Bidder Proposal Reference No.: |  |  |  | TH-14017 |  |  | EQ # 265386 | [5 empty] | (Do NOT delete BIDDER X)
| QCS Revision #/ Date: | Original | 2015-11-18 |  |  | Quoted Currency: |  |  |  | USD $ - US Dollar |  |  | USD $ - US Dollar |  |  | USD $ - US Dollar
| Project Currency: | USD $ - US Dollar |  |  |  | Exchange Rate (1 : xUSD $ - US Dollar) | 1 |  |  | 1 |  |  | 1 |  |  | 1 |  |  | 1
|  |  |  | TOTAL PROPOSAL PRICE | - | - | - | - | 0 | - | - | 895634.35 | - | - | 799235.12 | - | - | 963235.0575 | - | - | 0
|  | Pricing Breakdown |  |  | Qty. | Unit | Unit Price () | Definition | Total Price (USD $ - US Dollar) | Unit Price (USD $ - US Dollar) | Definition | Total Price (USD $ - US Dollar) | Unit Price (USD $ - US Dollar) | Definition | Total Price (USD $ - US Dollar) | Unit Price (USD $ - US Dollar) | Definition | Total Price (USD $ - US Dollar) | Unit Price () | Definition | Total Price (USD $ - US Dollar)
Pricing for Labor / Material |  |  |  |  | - | - | - | - | 0 | - | - | 790486.35 | - | - | 695343.12 | - | - | 822569.509 | - | - | 0 | USD - US Dollar, CAD - Canadian Dollar, AUD - Australian Dollar, EUR - Euro, GBP - British Pound, MXN - Mexican Peso, JPY - Japanese Yen, KRW - Korea Won, CNY - Chinese Yuan, INR - Indian Rupee
1 | Heat Trace Design/Engineering |  |  |  | 1 | LOT |  |  | 0 | 30956.08 | COST | 30956.08 | 13558.93 | COST | 13558.93 | 29680 | PLUG | 29680 |  |  | 0
2 | Equipment / Facilities / Safey |  |  |  | 1 | LOT |  |  | 0 | 120622.32 | COST | 120622.32 | 120622.32 | PLUG | 120622.32 |  |  | 0 |  |  | 0
3 | Heat Trace Material Cost |  |  |  | 1 | LOT |  |  | 0 | 294348 | COST | 294348 | 216601.92 | COST | 216601.92 | 297480.03 | PLUG | 297480.03 |  |  | 0
4 | Low-Temp Self-Regulating Heater Cable |  |  |  |  | ft |  |  | 0 | 4.3 | COST | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
5 | High-Temp Self-Regulating Heater Cable |  |  |  |  | ft |  |  | 0 |  | N/A | 0 | 3.9 | COST | 0 |  |  | 0 |  |  | 0
6 | MI Heater Cable |  |  |  |  | ft |  |  | 0 | 7.24 | COST | 0 | 4 | COST | 0 |  |  | 0 |  |  | 0
7 | MI Heater Cable Cold Lead |  |  |  |  | EA |  |  | 0 | 240 | COST | 0 | 145 | COST | 0 |  |  | 0 |  |  | 0
8 | Power Connection Enclosure w/ LED Light |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 135 | COST | 0 |  |  | 0 |  |  | 0
9 | MI Power Connection Enclosure |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 145 | COST | 0 |  |  | 0 |  |  | 0
10 | Power Connection Enclosure w/o LED Light |  |  |  |  | EA |  |  | 0 | 80.5 | COST | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
11 | End of circuit Termination w/ LED Light |  |  |  |  | EA |  |  | 0 | 136.5 | COST | 0 | 145 | COST | 0 |  |  | 0 |  |  | 0
12 | Power Termination Kit |  |  |  |  | PKG |  |  | 0 | 7.87 | COST | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
13 | Caution Labels (25 per pack) |  |  |  |  | PKG |  |  | 0 | 10.5 | COST | 0 | 125 | COST | 0 |  |  | 0 |  |  | 0
14 | Fixing Tape (36 yd roll) |  |  |  |  | PKG |  |  | 0 |  | N/A | 0 | 9 | COST | 0 |  |  | 0 |  |  | 0
15 | Hi Temp Fixing Tape (36 yd roll) |  |  |  |  | EA |  |  | 0 | 14.35 | COST | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
16 | Pipe Straps 10" |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 6 | COST | 0 |  |  | 0 |  |  | 0
17 | Pipe Straps 20" |  |  |  |  | EA |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
18 | Stainless Steel Circuit ID Tags |  |  |  |  | EA |  |  | 0 | 5.45 | COST | 0 | 175 | COST | 0 |  |  | 0 |  |  | 0
19 | Ambient Sensing RTD |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 200 | COST | 0 |  |  | 0 |  |  | 0
20 | Line Sensing RTD |  |  |  |  | EA |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
21 | Control and monitoring module |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 36000 | COST | 0 |  |  | 0 |  |  | 0
22 | 480-120/208V wye 75KVA Transformer |  |  |  |  | EA |  |  | 0 |  | N/A | 0 | 3500 | COST | 0 |  |  | 0 |  |  | 0
23 | 480-120/208V wye 45KVA Transformer |  |  |  |  | EA |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
24 | 480-120/208V wye 30KVA Transformer |  |  |  |  | EA |  |  | 0 | 1628.58 | COST | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
25 | 480-120/208V wye 15KVA Transformer |  |  |  |  | EA |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0 |  |  | 0
26 | Heat Trace Installation Labor |  |  |  | 1 | LOT |  |  | 0 | 344559.95 | PLUG | 344559.95 | 344559.95 | EXCL | 344559.95 | [5 empty] | 0
27 | Heat Trace Materials (Labor Only)
28 | Control Panels (UR from Homer City) |  |  |  | 3 | EA | [11 empty] | 3360.36
29 | Transformers (UR from La Cygne) |  |  |  | 3 | EA | [11 empty] | 3196.44
30 | Heat Trace (Self Regulating Cable, MI Cable. Accessories Included) (UR from Homer City) |  |  |  | 13604 | LF | [11 empty] | 44600.1404
31 | Electrical Materials
32 | Conduit (UR from La Cygne) |  |  |  | 6120 | LF | [11 empty] | 232097.328
33 | Wire and Cable (UR from La Cygne) |  |  |  | 30600 | LF | [11 empty] | 145607.04
34 | Terminations (UR from La Cygne) |  |  |  | 1224 | EA | [11 empty] | 35897.8392
35 | MH STS |  |  |  | 5573 | MH |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 30650.3314 |  |  | 0
28 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
29 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
30 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
31 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
32 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
33 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
34 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
35 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
36 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
37 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
38 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
39 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
40 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
41 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
42 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
43 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
44 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
45 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
46 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
47 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
48 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
49 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
50 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
51 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
52 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
53 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
54 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
55 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
56 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
57 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
58 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
59 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
60 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
61 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
62 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
63 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
64 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
65 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
66 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
67 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
68 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
69 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
70 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
71 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
72 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
73 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
74 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
75 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
76 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
77 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
78 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
79 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
80 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
81 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
82 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
83 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
84 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
85 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
86 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
87 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
88 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
89 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
90 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
91 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
92 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
93 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
94 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
95 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
96 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
97 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
98 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
99 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
100 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Pricing for Options Requested or Offered |  |  |  |  | - | - | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0
1 | Unit Adjusting Prices | [7 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | Price per Foot MI/ Cable |  |  |  |  | $/LF |  |  | 0 | 7.24 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | Price per Foot Low Temp Self Regulating Cable |  |  |  |  | $/LF |  |  | 0 | 4.3 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | Price per Foot High Temp Self Regulating Cable |  |  |  |  | $/LF |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | Cold Lead |  |  |  |  | $/EA |  |  | 0 | 240 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
6 | Power Termination Kit |  |  |  |  | $/EA |  |  | 0 | 80.5 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
7 | Splice Kit |  |  |  |  | $/EA |  |  | 0 | 80.5 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
8 | End of Circuit Light |  |  |  |  | $/EA |  |  | 0 | 136.5 |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
9 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
10 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Pricing for Standard Commercial Items |  |  |  |  | - | - | - | - | 0 | - | - | 18256 | - | - | 17000 | - | - | 53773.5485 | - | - | 0
1 | Sales/ Use Tax |  |  | Required | 1 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
2 | Freight (DDP Jobsite - Incoterms 2010) |  |  | Required | 1 | LOT |  |  | 0 | 8000 | COST | 8000 | 4000 | COST | 4000 | 23926.5589 | COST | 23926.5589 |  |  | 0
3 | Warranty - Standard (See 2.0 Below) |  |  | Required | 1 | LOT |  |  | 0 |  |  | 0 | 7500 | COST | 7500 | 17055.4226 | COST | 17055.4226 |  |  | 0
4 | Warranty - Adder to meet Owner's Terms (See 2.0 Below) |  |  | Not Required | 0 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
5 | TFA - Startup & Erection Assistance Duration (Bidder to specify quantity) |  |  | Not Required | 0 | DAY |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
6 | TFA - Startup & Erection Assistance Round Trip (Bidder to specify quantity) |  |  | Not Required | 0 | RT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
7 | TFA - Training Duration (Bidder to specify quantity) |  |  | Not Required | 0 | DAY |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
8 | TFA - Training Round Trip (Bidder to specify quantity) |  |  | Not Required | 0 | RT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
9 | Spares - Startup & Commissioning - (Bidder to provide detailed list) |  |  | Not Required | 0 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
10 | Spares - Construction - (Bidder to provide detailed list) |  |  | Not Required | 0 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
11 | Spares - Special Tools - (Bidder to provide detailed list) |  |  | Not Required | 0 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
12 | Spares - 2-Year Operating - (Bidder to provide detailed list) |  |  | Not Required | 0 | LOT |  |  | 0 |  | N/A | 0 |  | N/A | 0 |  | N/A | 0 |  |  | 0
13 | Security Cost (Bond for full contract price, Letter of Credit, Etc.) |  |  | Required | 1 | LOT |  |  | 0 | 10256 | COST | 10256 | 5500 | COST | 5500 | 12791.567 | COST | 12791.567 |  |  | 0
Commercial Adjustments |  |  |  |  | - | - | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0
1 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Technical Adjustments |  |  |  |  | - | - | - | - | 0 | - | - | 86892 | - | - | 86892 | - | - | 86892 | - | - | 0
1 | Boiler Feed Water Pump HT (Based on Woodbridge) |  |  |  | 2 | EA |  |  | 0 | 43446 |  | 86892 | 43446 |  | 86892 | 43446 |  | 86892 |  |  | 0
2 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [8 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
TOTAL PROPOSAL PRICE |  |  |  |  | - | - | - | - | 0 | - | - | 895634.35 | - | - | 799235.12 | - | - | 963235.0575 | - | - | 0
TOTAL PROPOSAL PRICE (Not Including Security) |  |  |  |  | - | - | - | - | 0 | - | - | 885378.35 | - | - | 793735.12 | - | - | 950443.4905 | - | - | 0
TOTAL UNIT PRICE (Not Including Security) - Enter In Hard Dollar | [5 empty] | - | - | - |  | - | - |  | - | - |  | - | - |  | - | -
Security Cost Per $1000 - Enter In Hard Dollar |  |  |  |  | - | Per $1000 | - | - |  | - | - | 11.5837 | - | - | 6.9293 | - | - | 13.4585 | - | -
Evaluation Factors (constructability, past performance, etc.) |  |  |  |  | - | - | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0
1 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
TOTAL EVALUATED PRICE |  |  |  |  | - | - | - | - | 0 | - | - | 895634.35 | - | - | 799235.12 | - | - | 963235.0575 | - | - | 0
Options Excluded |  |  |  |  | - | - | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0 | - | - | 0
1 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
2 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
3 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
4 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
5 | [5 empty] | LOT |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0
Commercial Requirements
1.0 Financial Security
| Specify type of security instrument provided (select from drop-down list) | [8 empty] | 100% Payment & Performance Bond |  |  | 100% Supply Bond
| Rate per $1,000 of coverage: | [8 empty] | 16
| Bidder's Surety Firm: | [8 empty] | Argonaut Ins. Company |  |  | Zurich
| Bonding Capacity: | [8 empty] | 30000000 |  |  | Not Provided
2.0 Warranty
| Specify Bidder's Standard Warranty terms included in Bidder's Base Price | [8 empty] | Yes |  |  | Yes
| Confirm Standard Warranty with price Adder above will meet Owner's terms of 12 months from Substantial | [8 empty] | Confirmed |  |  | Confirmed
| Completion of: | 2019-06-01 | Note: Rework warranty is 12 months from rework date but shall be capped at 24 months from Substantial Completion date. | [6 empty] | 12 Months |  |  | 24 Months from substantial completion
3.0 Site Specific Requirements
| Is Safety training and orientation included in your proposal? (select from drop-down list) | [8 empty] | Yes |  |  | No
| Are background checks included in your proposal? | [8 empty] | No |  |  | No
| Are employee drug testing costs included in your proposal? | [8 empty] | No |  |  | No
4.0 Lead Time and Schedule of Work
| Lead Time - Drawings ARO (Include 2 Weeks for Drawing Approval) | [8 empty] | 14 Weeks |  |  | 4 Weeks
| Lead Time - Equipment/Material to Jobsite ARAD | [8 empty] | 10 Weeks |  |  | 6 Weeks
| Lead Time - Installation / Erection (mobilization to demobilization) | [8 empty] | 10 Weeks
| Schedule - Number of Craft Workers required | [8 empty] | 10
| Schedule - Hours worked per day | [6 empty] | 10 |  | 10 |  |  | 10
| Schedule - Number of days worked per week | [6 empty] | 5 |  | 5 |  |  | 5
| Schedule - Total estimated man-hours | [8 empty] | 4614
| Labor - Union or Non-Union | [8 empty] | Non-Union
5.0 Bidder Certification - Technical, Business, Diversity, Etc.
Bidder's Primary Certification (select from drop-down list)
Additional Certification (select from drop-down list)
6.0 Proposal Requirements - Insurance, Safety, Quality, and Licensing
| Can Bidder meet Insurance requirements as specified in RFP? (select from drop-down list) | [8 empty] | Yes |  |  | Yes
| Does Bidder have written Quality Assurance program? (select from drop-down list) | [8 empty] | Yes |  |  | Yes
| Does Bidder have written Safety Program? (select from drop-down list) | [8 empty] | Yes |  |  | Yes
| EMR and Frequency/Severity Rates for last 3 years | [5 empty] | Current Year | Year 2 | Year 3 | Current Year | Year 2 | Year 3 | Current Year | Year 2 | Year 3 | Current Year | Year 2 | Year 3 | Current Year | Year 2 | Year 3
[6 empty] | EMR Rates: |  |  |  | 0.63 | 0.6 | 0.58
[6 empty] | Frequency / Severity Rates: |  |  |  | 0 | 0 | 0
| Is your Company currently licensed in the State where Project is located? | [8 empty] | No
7.0 Proposal Exception
| Does Bidder Proposal comply with Instructions to Bidders? (select from drop-down list) | [8 empty] | Yes
8.0 Proposed Progress Payment Milestones | [6 empty] | Description of Milestone |  | % of Contract Price | Description of Milestone |  | % of Contract Price | Description of Milestone |  | % of Contract Price | Description of Milestone |  | % of Contract Price | Description of Milestone |  | % of Contract Price
[6 empty] | 1st Milestone | [6 empty] | with purchase order |  | 20%
[6 empty] | 2nd Milestone | [6 empty] | substantial eng completion |  | 20%
[6 empty] | 3rd Milestone | [6 empty] | at time of shipment
4th Milestone
5th Milestone
6th Milestone
7th Milestone
8th Milestone
9th Milestone
10th Milestone
Technical Design Conditions |  |  |  |  | Per RFP/ EPC Contract |  | - |  |  | - |  |  | - |  |  | - |  |  | -
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
Additional Technical and Commercial Information/Clarifications/Exceptions | [6 empty] | - |  |  | - |  |  | - |  |  | - |  |  | -
1
2
3
4
5
[6 empty] | Pricing Reliability Indicator (Low Plug = High Reliability) | - |  |  | - |  |  | - |  |  | - |  |  | -
1 | [6 empty] | Plug $ | Plug % | Total Price | Plug $ | Plug % | Total Price | Plug $ | Plug % | Total Price | Plug $ | Plug % | Total Price | Plug $ | Plug % | Total Price
[6 empty] | Amount and % of plugs: | 0 |  | 0 | 344559.95 | 38.47% | 895634.35 | 120622.32 | 15.09% | 799235.12 | 327160.03 | 33.96% | 963235.0575 | 0 |  | 0
[6 empty] | Total Proposal Price Comparison | - |  |  | - |  |  | - |  |  | - |  |  | -
1 | [5 empty] | Amount above minimum bid: | [5 empty] | 96399.23 |  |  | 0 |  |  | 163999.9375
2 | [5 empty] | Percent above minimum bid: | [5 empty] | 12.06% |  |  | 0% |  |  | 20.52%
[6 empty] | Awarding | - |  |  | - |  |  | - |  |  | - |  |  | -
1 | [5 empty] | Technically Acceptable ("Yes"/"No")
2 | [5 empty] | If No, Explain…
3 | [5 empty] | Commercially Acceptable ("Yes"/"No") |  |  |  | NO |  |  | YES |  |  | YES
4 | [5 empty] | If No, Explain…
5 | [5 empty] | Price Carried In Estimate ("Yes"/"No") | [9 empty] | YES
6 | [5 empty] | If technically and commercially acceptable but low price is not carried, Explain…
7 | [5 empty] | Alternate Price ("Yes"/"No") | [6 empty] | YES
8 | [5 empty] | If technically and commercially acceptable but next low price is not an alternate, Explain…
9 | IMPORTANT: Enter additional notes that will help others (now and many monthss into the future) understand fully the team's evaluation, observation and reasoning (without having to track someone down or relying on one's memories) | [8 empty] | Plugged Kiewit Self Perform Labor |  |  | ***NO Labor*** Total Bid $216,580 |  |  | Plugged Thermons Material Cost
SALES/ USE TAX CALCULATOR:
[6 empty] | (Indirect Lead will use this information to determine sales/ use tax adjustment) |  | Material Cost: | 0 |  | Material Cost: | 0 |  | Material Cost: | 0 |  | Material Cost: | 0 |  | Material Cost: | 0
[8 empty] | Sales/ Use Tax $: | 0 |  | Sales/ Use Tax $: | 0 |  | Sales/ Use Tax $: | 0 |  | Sales/ Use Tax $: | 0 |  | Sales/ Use Tax $: | 0
[8 empty] | Sales/Use Tax % (Calculated): |  |  | Sales/Use Tax % (Calculated): |  |  | Sales/Use Tax % (Calculated): |  |  | Sales/Use Tax % (Calculated): |  |  | Sales/Use Tax % (Calculated):
[8 empty] | Kiewit %: | 0% |  | Kiewit %: | 0% |  | Kiewit %: | 0% |  | Kiewit %: | 0% |  | Kiewit %: | 0%
[8 empty] | Kiewit Sales/ Use Tax $ (Cal.): | 0 |  | Kiewit Sales/ Use Tax $ (Cal.): | 0 |  | Kiewit Sales/ Use Tax $ (Cal.): | 0 |  | Kiewit Sales/ Use Tax $ (Cal.): | 0 |  | Kiewit Sales/ Use Tax $ (Cal.): | 0
DO NOT DELETE - USED FOR BID FORM - KEEP AT LINE 599 FOR MACROS
The undersigned agrees, if this bid is accepted, to enter into a contract with Contractor in accordance with the terms and conditions outlined in the attached sample contract for the work described in the Instructions to Bidders and any subsequent addenda. Any and all deviations and/or exceptions taken by bidder to the terms, conditions, plans, specifications, codes, standards or this request for quote shall be clearly stated in writing and included as an attachment to the bid form.
Name/ Title | [6 empty] | Date
Company Name | [6 empty] | Contact Phone
Address | [6 empty] | Email
Formulas:
Advanced Power = [1]ITB!$D214
Note on I2: Supplier on AVL: Supplier is on Owner-provided AVL. Not on AVL: Supplier not on Owner-provided AVL. No AVL: Owner did not provide AVL. AVL: Approved Vendor List.
Note on J2: Risk $: risk money is required to carry this price/supplier. Do not add risk money to QCS. See Risk Log for amount.
Note on K2: Need Awarding: Go to Awarding section at bottom to make your selection. Delete unneeded (empty) Bidder columns). Carried: Price is carried in estimate or selected for purchase. Alternate: Next best price to carry in estimate or to purchase. Carried & Alternate: Only one price is available or other prices are not feasible alternates.
Note on L2: Supplier on AVL: Supplier is on Owner-provided AVL. Not on AVL: Supplier not on Owner-provided AVL. No AVL: Owner did not provide AVL. AVL: Approved Vendor List.
Note on M2: Risk $: risk money is required to carry this price/supplier. Do not add risk money to QCS. See Risk Log for amount.
Note on N2: Need Awarding: Go to Awarding section at bottom to make your selection. Delete unneeded (empty) Bidder columns). Carried: Price is carried in estimate or selected for purchase. Alternate: Next best price to carry in estimate or to purchase. Carried & Alternate: Only one price is available or other prices are not feasible alternates.
Note on O2: Supplier on AVL: Supplier is on Owner-provided AVL. Not on AVL: Supplier not on Owner-provided AVL. No AVL: Owner did not provide AVL. AVL: Approved Vendor List.
Note on P2: Risk $: risk money is required to carry this price/supplier. Do not add risk money to QCS. See Risk Log for amount.
Note on Q2: Need Awarding: Go to Awarding section at bottom to make your selection. Delete unneeded (empty) Bidder columns). Carried: Price is carried in estimate or selected for purchase. Alternate: Next best price to carry in estimate or to purchase. Carried & Alternate: Only one price is available or other prices are not feasible alternates.
Note on R2: Supplier on AVL: Supplier is on Owner-provided AVL. Not on AVL: Supplier not on Owner-provided AVL. No AVL: Owner did not provide AVL. AVL: Approved Vendor List.
Note on S2: Risk $: risk money is required to carry this price/supplier. Do not add risk money to QCS. See Risk Log for amount.
Note on T2: Need Awarding: Go to Awarding section at bottom to make your selection. Delete unneeded (empty) Bidder columns). Carried: Price is carried in estimate or selected for purchase. Alternate: Next best price to carry in estimate or to purchase. Carried & Alternate: Only one price is available or other prices are not feasible alternates.
Note on U2: Supplier on AVL: Supplier is on Owner-provided AVL. Not on AVL: Supplier not on Owner-provided AVL. No AVL: Owner did not provide AVL. AVL: Approved Vendor List.
Note on V2: Risk $: risk money is required to carry this price/supplier. Do not add risk money to QCS. See Risk Log for amount.
Note on W2: Need Awarding: Go to Awarding section at bottom to make your selection. Delete unneeded (empty) Bidder columns). Carried: Price is carried in estimate or selected for purchase. Alternate: Next best price to carry in estimate or to purchase. Carried & Alternate: Only one price is available or other prices are not feasible alternates.
Note on L3: You may enter date in mm/dd/yyyy format.
Note on O3: You may enter date in mm/dd/yyyy format.
Note on R3: You may enter date in mm/dd/yyyy format.
Note on U3: You may enter date in mm/dd/yyyy format.
Note on L4: You may enter date in mm/dd/yyyy format.
Note on O4: You may enter date in mm/dd/yyyy format.
Note on R4: You may enter date in mm/dd/yyyy format.
Note on U4: You may enter date in mm/dd/yyyy format.
Note on I11: You may enter date in mm/dd/yyyy format.
Note on L11: You may enter date in mm/dd/yyyy format.
Note on O11: You may enter date in mm/dd/yyyy format.
Note on R11: You may enter date in mm/dd/yyyy format.
Note on U11: You may enter date in mm/dd/yyyy format.
Note on I12: You may enter date in mm/dd/yyyy format.
Note on L12: You may enter date in mm/dd/yyyy format.
Note on O12: You may enter date in mm/dd/yyyy format.
Note on R12: You may enter date in mm/dd/yyyy format.
Note on U12: You may enter date in mm/dd/yyyy format.
Note on B191: Warranty duration and Substantial Completion date came from data specified on ITB
Note on H444: Individual bidder prices are not compared with "Combined Selection" price. But "Combined Selection" price is compared with individual bidder prices.
Note on H445: % will show when all unused bidder columns are deleted. You may retain Bidder X for future insert. 0% indicates lowest price.

## Heat Trace QCS (hidden)
QUOTE COMPARISON SHEET - SUBCONTRACT
Primary DOR: Technical Staff pink sections, Procurement Staff everything else. | [5 empty] | Owner AVL Status:
SUB - Heat Trace | [5 empty] | BID DUE: | [7 empty] | 2014-06-20 |  |  |  | 2014-06-20 |  |  |  |  | 2014-06-20
[7 empty] | KIEWIT DESIGN AND INSTALL | [6 empty] | 2014-06-05 |  |  |  | 2014-06-05 |  |  |  |  | 2014-06-05
[17 empty] | Days |  | 15 |  |  | Days |  | 15 |  |  | Days
| Project No.: | [5 empty] | Self Performed | [6 empty] | BIDDER 1 |  |  |  | BIDDER 2 |  |  |  |  | BIDDER 3
| Project Name: |  |  |  |  | Bidder Legal Name: | HISTORICAL
| Owner: |  |  |  |  | Bidder Contact Name:
| Job Site: |  |  |  |  | Bidder Contact Email:
| RFP Description: | Heat Trace |  |  |  | Bidder Phone:
| Spec: | SUB |  |  |  | Bid Date or "No Bid":
| HD Quote Group Tag: |  |  |  |  | Bid Valid Until Date:
| Engineering: |  |  |  |  | Bid Validity Duration (Days): | 0
| Procurement: |  |  |  |  | Firm or Budgetary Bid:
| Reviewer: |  |  |  |  | Bidder Proposal Reference No.:
| QCS Revision #/ Date: | A |  |  |  | Quoted Currency: | USD - US Dollar | [6 empty] | USD - US Dollar |  |  |  | USD - US Dollar |  |  |  |  | USD - US Dollar
| Project Currency: | USD - US Dollar |  |  |  | Exchange Rate (1 : $xUSD - US Dollar) | Enter Project Currency In Cell D17 | [6 empty] | Enter Project Currency In Cell D17 |  |  |  | Enter Project Currency In Cell D17 |  |  |  |  | Enter Project Currency In Cell D17
TOTAL PROPOSAL PRICE |  |  |  |  | - | - | - | - | - |  | - | - | #VALUE! | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
Pricing Breakdown |  |  |  |  | Qty. | Unit | Unit Rate | Manhours | $/MH | Labor Total | Unit Cost | Material Total | Total Price () | Unit Price (USD - US Dollar) | Labor Total | Material Total | Total Price () | Unit Price (USD - US Dollar) | Definition | Labor Total | Material Total | Total Price () | Unit Price (USD - US Dollar) | Definition | Labor Total | Material Total | Total Price ()
Labor / Material Quoted |  |  |  |  | - | - | - | - | - |  | - | - | 987311.5788 | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE! | Heat Trace Design/Engineering | 126350
1 | Heat Trace Design/Engineering |  |  |  | 361 | EA |  |  | 350 | 126350 |  |  | 126350 | [14 empty] | Equipment / Facilities / Safety | 65835.7752
2 | Heat Trace Materials | [11 empty] | 0 | [14 empty] | Heat Trace Material Cost | 15000
3 | Control Panels (UR from Homer City) |  |  |  | 9 | EA | 15 | 135 | 58.5369 | 7902.48 |  | 0 | 7902.48 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Heat Trace Installation Labor Cost | 780125.8036
4 | Transformers (UR from La Cygne) |  |  |  | 9 | EA | 15 | 135 | 58.5369 | 7902.48 |  | 0 | 7902.48 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Total Cost | 987311.5788
5 | Heat Trace (Self Regulating Cable, MI Cable. Accessories Included) (UR from Homer City) |  |  |  | 24599 | LF | 0.3 | 7379.7 | 58.5369 | 431984.6803 |  | 0 | 431984.6803 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
6 | Heat Trace Accessories - Vendor Pipe |  |  |  | 1 | LOT |  |  |  |  | 15000 | 15000 | 15000
7 | Electrical Materials
8 | Conduit (UR from La Cygne) |  |  |  | 7220 | LF | 0.449 | 3241.78 | 58.5369 | 189763.7163 |  | 0 | 189763.7163 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
9 | Wire and Cable (UR from La Cygne) |  |  |  | 36400 | LF | 0.038 | 1383.2 | 58.5369 | 80968.225 |  | 0 | 80968.225 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
10 | Wire and Cable RTD (UR from La Cygne) |  |  |  | 3000 | LF | 0.038 | 114 | 58.5369 | 6673.2054 |  | 0 | 6673.2054
11 | Terminations (UR from La Cygne) |  |  |  | 2346 | EA | 0.4 | 938.4 | 58.5369 | 54931.0167 |  | 0 | 54931.0167 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
12 | MH STS |  |  |  | 13327.08 | MH |  |  | 4.94 |  |  |  | 65835.7752
13 | [12 empty] | 0
14 | [12 empty] | 0
15 | [12 empty] | 0
14 | [12 empty] | 0
15 | [12 empty] | 0
16 | [12 empty] | 0
17 | [12 empty] | 0
18 | [12 empty] | 0
19 | [12 empty] | 0
20 | [12 empty] | 0
21 | [12 empty] | 0
22 | [12 empty] | 0
23 | [12 empty] | 0
24 | [12 empty] | 0
25 | [12 empty] | 0
26 | [12 empty] | 0
27 | [12 empty] | 0
28 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
29 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
30 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
31 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
32 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
33 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
34 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
35 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
36 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
37 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
38 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
39 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
40 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
41 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
42 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
43 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
44 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
45 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
46 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
47 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
48 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
49 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
50 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
51 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
52 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
53 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
54 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
55 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
56 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
57 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
58 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
59 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
60 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
61 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
62 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
63 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
64 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
65 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
66 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
67 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
68 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
69 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
70 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
71 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
72 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
73 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
74 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
75 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
76 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
77 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
78 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
79 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
80 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
81 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
82 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
83 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
84 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
85 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
86 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
87 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
88 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
89 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
90 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
91 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
92 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
93 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
94 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
95 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
96 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
97 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
98 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
99 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
100 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
Options Requested or Offered | [5 empty] | - | - | - | - |  | - | - | 0 | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
1 | Warranty - for 1 Year beyond Owner's Requirement |  |  |  |  | LOT | [6 empty] | 0
2 | [12 empty] | 0
3 | Cost (included above) of HRSG Heat Trace Scope of Work ONLY: |  |  |  |  | LOT | [6 empty] | 0
4 | Turn Key Adder per proposal - Conduit, cable, and supports |  |  |  |  | LOT | [6 empty] | 0
5 | [5 empty] | LOT | [6 empty] | 0
6 | [5 empty] | LOT | [6 empty] | 0
7 | [5 empty] | LOT | [6 empty] | 0
8 | [5 empty] | LOT | [6 empty] | 0
9 | [5 empty] | LOT | [6 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
10 | [5 empty] | LOT | [6 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
Standard Commercial Items | [5 empty] | - | - | - | - |  | - | - | 35305.9053 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | Sales/ Use Tax |  |  | Not Required |  | LOT | [6 empty] | 0
2 | Freight (DDP Jobsite - Incoterms 2010) (5% of Material $) |  |  | Required | 1 | LOT | 750 | [5 empty] | 750
3 | Warranty - Standard (See 2.0 Below) (2% of total $) |  |  | Required | 1 | LOT | 19746.2316 | [5 empty] | 19746.2316
4 | Warranty - Adder to meet Owner's Terms (See 2.0 Below) |  |  | Required |  | LOT | [6 empty] | 0
5 | TFA - Startup & Erection Assistance Duration (Bidder to specify quantity) |  |  | Required |  | DAY | [6 empty] | 0
6 | TFA - Startup & Erection Assistance Round Trip (Bidder to specify quantity) |  |  | Required |  | RT | [6 empty] | 0
7 | TFA - Training Duration (Bidder to specify quantity) |  |  | Required |  | DAY | [6 empty] | 0
8 | TFA - Training Round Trip (Bidder to specify quantity) |  |  | Required |  | RT | [6 empty] | 0
9 | Spares - Startup & Commissioning - (Bidder to provide detailed list) |  |  | Required |  | LOT | [6 empty] | 0
10 | Spares - Construction - (Bidder to provide detailed list) |  |  | Required |  | LOT | [6 empty] | 0
11 | Spares - Special Tools - (Bidder to provide detailed list) |  |  | Required |  | LOT | [6 empty] | 0
12 | Spares - 2-Year Operating - (Bidder to provide detailed list) |  |  | Not Required |  | LOT | [6 empty] | 0
13 | Security Cost (Bond for full contract price, Letter of Credit, Etc.) (1.5% of total $) |  |  | Required | 1 | LOT | 14809.6737 | [5 empty] | 14809.6737
Commercial Adjustments | [5 empty] | - | - | - | - |  | - | - | 0 | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
1 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
2 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
3 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
4 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
5 | [12 empty] | 0 |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
Technical Adjustments |  |  |  |  | - | - | - | - | - |  | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
[6 empty] | LOT | [6 empty] | 0
[6 empty] | LOT | [6 empty] | 0
[6 empty] | LOT | [6 empty] | 0
[6 empty] | LOT | [6 empty] | 0
[6 empty] | LOT | [6 empty] | 0
TOTAL PROPOSAL PRICE |  |  |  |  | - | - | - | - | - |  | 0 | 0 | #VALUE! | #REF! | #VALUE! | #REF! | #VALUE! | - | - | #VALUE! | #REF! | #VALUE! | - | - | #VALUE! | #REF! | #VALUE!
TOTAL PROPOSAL PRICE (Not Including Security) |  |  |  |  | - | - | - | - | - |  | - | - | #VALUE! | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
TOTAL UNIT PRICE (Not Including Security) - Enter In Hard Dollar | [5 empty] | - | - | - | - |  | - | - | #VALUE! | - | - | - |  | - | - | - | - |  | - | - | - | -
Security Cost Per $1000 - Enter In Hard Dollar |  |  |  |  | - | Per $1000 | - | - | - |  | - | - | #VALUE! | - | - | - |  | - | - | - | - |  | - | - | - | -
Evaluation Factors (constructability, past performance, etc.) |  |  |  |  | - | - | - | - | - |  | - | - | #VALUE! | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
1 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
2 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
3 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
4 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
5 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
TOTAL EVALUATED PRICE |  |  |  |  | - | - | - | - | - |  | - | - | #VALUE! | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
Options Excluded |  |  |  |  | - | - | - | - | - |  | - | - | #VALUE! | - | - | - | #VALUE! | - | - | - | - | #VALUE! | - | - | - | - | #VALUE!
1 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
2 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
3 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
4 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
5 | [5 empty] | LOT | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
Commercial Items Requirements
1.0 Financial Security
| Specify type of security instrument provided (select from drop-down list) | [12 empty] | 100% Supply Bond |  |  |  | 100% Supply Bond |  |  |  |  | 100% Supply Bond
| Rate per $1,000 of coverage: | [12 empty] | Not Provided - Plugged 1.5% for 100% Bond |  |  |  | Not Provided - Plugged 1.5% for 100% Bond |  |  |  |  | Not Provided - Plugged 1.5% for 100% Bond
| Bidder's Surety Firm: | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Bonding Capacity: | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
2.0 Warranty
| Specify Bidder's Standard Warranty terms included in Bidder's Base Price | [12 empty] | 12 mo. From delivery / plug 2% for add'l yr |  |  |  | 12 mo. From delivery / plug 2% for add'l yr |  |  |  |  | 12 mo. From delivery / plug 2% for add'l yr
| Confirm Standard Warranty with price Adder above will meet Owner's terms of 12 months from Substantial | [12 empty] | Confirmed |  |  |  | Confirmed |  |  |  |  | Confirmed
| Completion of: | Summer 2017
3.0 Site Specific Requirements
| Is Safety training and orientation included in your proposal? (select from drop-down list) | [12 empty] | No |  |  |  | No |  |  |  |  | No
| Are background checks included in your proposal? | [12 empty] | No - see attached comments |  |  |  | No - see attached comments |  |  |  |  | No - see attached comments
| Are employee drug testing costs included in your proposal? | [12 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
[14 empty] | Supply Only |  |  |  | Supply Only |  |  |  |  | Supply Only
4.0 Shipping and Schedule of Work
| Lead Time - Drawings ARO (Include 2 Weeks for Drawing Approval) | [12 empty] | 6-8 weeks |  |  |  | 6-8 weeks |  |  |  |  | 6-8 weeks
| Lead Time - Equipment/Material to Jobsite ARAD | [12 empty] | 10-12 weeks |  |  |  | 10-12 weeks |  |  |  |  | 10-12 weeks
| Lead Time - Installation / Erection (mobilization to demobilization) | [12 empty] | 16-20 weeks |  |  |  | 16-20 weeks |  |  |  |  | 16-20 weeks
| Schedule - Number of Craft Workers required | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Hours worked per day | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Number of days worked per week | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Total estimated man-hours | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Labor - Union or Non-Union | [12 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
5.0 Bidder Certification - Technical, Business, Diversity, Etc.
Bidder's Primary Certification (select from drop-down list)
Additional Certification (select from drop-down list)
6.0 Proposal Requirements - Insurance, Safety, Quality, and Licensing
| Can Bidder meet Insurance requirements as specified in RFP? (select from drop-down list) | [12 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| Does Bidder have written Quality Assurance program? (select from drop-down list) | [12 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| Does Bidder have written Safety Program? (select from drop-down list) | [12 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| EMR and Frequency/Severity Rates for last 3 years | [5 empty] | Year 1 | Year 1 | Year 1 |  | Year 1 | Year 1 | Year 3 | Year 1 | Year 1 | Year 1 | Year 3 | Year 1 | Year 2 | Year 1 | Year 1 | Year 3 | Year 1 | Year 2 | Year 1 | Year 1 | Year 3
EMR Rates:
Frequency / Severity Rates:
Is your Company currently licensed in the State where Project is located?
[14 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
7.0 Proposal Exception
| Does Bidder Proposal comply with Instructions to Bidders? (select from drop-down list) | [12 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
8.0 Proposed Progress Payment Milestones |  |  |  | Percentage of Contract Total |  |  | Description of Milestone |  |  |  | Description of Milestone |  | % of Contract Price | Description of Milestone |  |  | % of Contract Price | Description of Milestone |  |  |  | % of Contract Price | Description of Milestone |  |  |  | % of Contract Price
1st Milestone
| 2nd Milestone | 2nd Milestone
| 3rd Milestone | 3rd Milestone
| 4th Milestone | 4th Milestone
| 5th Milestone | 5th Milestone
| 6th Milestone | 6th Milestone
| 7th Milestone | 7th Milestone
| 8th Milestone | 8th Milestone
| 9th Milestone | 9th Milestone
| 10th Milestone | 15th Milestone
Technical Design Conditions |  |  |  | Per RFP/ EPC Contract |  |  | - | [6 empty] | - |  |  |  | - |  |  |  |  | -
1 | Westmoreland:
2 | Total LF Pipe: |  | 18383
3 | Total $/LF: |  | #VALUE!
4
5 | St. Joe
6 | Total LF Pipe: |  | 41374
7 | Proposal Price: |  | 2383422
8 | Total $/LF: |  | 57.6068
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
Additional Technical and Commercial Information/Clarifications/Exceptions | [6 empty] | - | [6 empty] | - |  |  |  | - |  |  |  |  | -
1
2
3
4
5
Comparison of Total Proposal Prices | [6 empty] | - | [6 empty] | - |  |  |  | - |  |  |  |  | -
1 | [5 empty] | Amount above minimum bid: | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
2 | [5 empty] | Percent above minimum bid: | [6 empty] | #VALUE! |  |  |  | #VALUE! |  |  |  |  | #VALUE! |  |  |  |  | #VALUE!
Pricing Reliability Indicator (Low Plug = High Reliability) | [6 empty] | - | [6 empty] | - |  |  |  | - |  |  |  |  | -
1 | Dollar and % of Amount Plugged | [5 empty] | Plug $ | Plug $ | Plug $ |  | Plug $ | Plug $ | Total Price | Plug $ | Plug $ | Plug $ | Total Price | Plug $ | Plug % | Plug $ | Plug $ | Total Price | Plug $ | Plug % | Plug $ | Plug $ | Total Price
[7 empty] | #REF! | 0 | #REF! |  | #REF! | #REF! | #VALUE! | #REF! | #REF! | #REF! | #VALUE! | 0 |  | #REF! | #REF! | #VALUE! | 0 |  | #REF! | #REF! | #VALUE!
Awarding | [6 empty] | - | [6 empty] | - |  |  |  | - |  |  |  |  | -
1 | Technically Acceptable ("Yes"/"No") | [12 empty] | YES |  |  |  | YES |  |  |  |  | YES
2 | If No, Explain…
3 | Commercially Acceptable ("Yes"/"No") | [12 empty] | YES |  |  |  | YES |  |  |  |  | YES
4 | If No, Explain…
5 | Price Carried In Estimate ("Yes"/"No")
6 | If technically and commercially acceptable but low price is not carried, Explain…
7 | Alternate Price ("Yes"/"No")
8 | If technically and commercially acceptable but next low price is not an alternate, Explain…
9 | Enter any additional notes that might help others (now and many years into the future) understand fully the team's evaluation, observation and reasoning (without having to track someone down or relying on one's memories)

## System Maintain Temperatures (hidden)
System | Maintain Temp | RTD10CS | RTD4AL | 910*E1WL*SSR2
ACW | 40 | 0 | 0 | 0
AQA | 40 | 0 | 0 | 0
ARM | 40 | 0 | 0 | 0
ARR | 40 | 0 | 0 | 0
AXS | 40 | 0 | 0 | 0
BDN | 40 | 0 | 0 | 0
BFW | 40 | 0 | 0 | 0
CCF | 60 | 0 | 0 | 0
CCW | 40 | 0 | 0 | 0
CDN | 40 | 0 | 0 | 0
CMG | 40 | 0 | 0 | 0
CND | 40 | 0 | 0 | 0
CPS | 40 | 0 | 0 | 0
CRH | 40 | 0 | 0 | 0
CTG | 40 | 0 | 0 | 0
CTP | 40 | 0 | 0 | 0
CWS | 40 | 0 | 0 | 0
DWS | 60 | 0 | 0 | 0
DWT | 65 | 1 | 1 | 1
FGA | 40 | 0 | 0 | 0
FGS | 100 | 1 | 1 | 1
FPA | 60 | 0 | 0 | 0
FPS | 40 | 0 | 0 | 0
HOS | 40 | 0 | 0 | 0
HPS | 40 | 0 | 0 | 0
HRH | 40 | 0 | 0 | 0
INA | 40 | 0 | 0 | 0
LOS | 40 | 0 | 0 | 0
LPS | 40 | 0 | 0 | 0
PDR | 40 | 0 | 0 | 0
PWS | 60 | 1 | 1 | 1
RHS | 40 | 0 | 0 | 0
RWS | 40 | 0 | 0 | 0
SDR | 60 | 0 | 0 | 0
SMP | 40 | 0 | 0 | 0
SOS | 40 | 0 | 0 | 0
STG | 40 | 0 | 0 | 0
STP | 40 | 0 | 0 | 0
SVA | 40 | 0 | 0 | 0
SWS | 60 | 0 | 0 | 0
SWT | 40 | 0 | 0 | 0
TCF | 40 | 0 | 0 | 0
WCF | 40 | 0 | 0 | 0
WDR | 40 | 0 | 0 | 0
WWT | 60 | 0 | 0 | 0
FOL | 100 | 1 | 1 | 1

## Cable Types (hidden)
Cat Number | Power Output | Heating Cable Family | Design Temperature | Unit | Max Circuit Length | Start Up Temperature | Breaker Size |  | Cable Family | Max Power Output | Design Temp
10BTV1-CT | 10 | BTV | 140 | FT | 170 | -40 | 40 |  | XTV | 20 | 250
8BTV1-CT | 8 | BTV | 140 | FT | 210 | -40 | 40 |  | BTV | 10 | 140
5BTV1-CT | 5 | BTV | 140 | FT | 270 | -40 | 40 |  | QTVR | 20 | 225
3BTV1-CT | 3 | BTV | 140 | FT | 330 | -40 | 40 |  | VPL | 20 | 360
20QTVR-CT | 20 | QTVR | 225 | FT | 110 | -40 | 40
15QTVR1-CT | 15 | QTVR | 225 | FT | 135 | -40 | 40 |  | Cable Family | Min Power Output | Design Temp
10QTVR1-CT | 10 | QTVR | 225 | FT | 180 | -40 | 40 |  | XTV | 5 | 250
20VPL1-CT | 20 | VPL | 360 | FT | 160 | -40 | 40 |  | BTV | 3 | 140
15VPL1-CT | 15 | VPL | 360 | FT | 210 | -40 | 40 |  | QTVR | 10 | 225
10VPL1-CT | 10 | VPL | 360 | FT | 260 | -40 | 40 |  | VPL | 5 | 360
5VPL1-CT | 5 | VPL | 360 | FT | 370 | -40 | 40
20XTV-CT | 20 | XTV | 250 | FT | 130 | -40 | 40
15XTVR1-CT-T3 | 15 | XTV | 250 | FT | 165 | -40 | 40
10XTV1-CT-T3 | 10 | XTV | 250 | FT | 240 | -40 | 40
5XTVR1-CT-T2 | 5 | XTV | 250 | FT | 385 | -40 | 40
Cable | Resistance (Ω/ft) | Cable Diameter (in) | Max Circuit Length (LF) | Nominal Weight (lb/1000 ft) |  |  | Cable | Resistance (Ω/ft) | Cable Diameter (in) | Max Circuit Length (LF) | Nominal Weight (lb/1000 ft)
32SF1110 | 11 | 0.13 | 2283 | 28 |  |  | 62SF1110 | 11 | 0.194 | 1023 | 61
32SF2900 | 9 | 0.14 | 1969 | 32 |  |  | 62SF2900 | 9 | 0.194 | 1024 | 61
32SF2750 | 7.5 | 0.157 | 1565 | 41 |  |  | 62SF2600 | 6 | 0.194 | 1025 | 62
32SA2600 | 6 | 0.135 | 2121 | 30 |  |  | 62SA2414 | 4.14 | 0.215 | 834 | 76
32SA2400 | 4 | 0.16 | 1816 | 36 |  |  | 62SF2200 | 2 | 0.245 | 644 | 100
32SA2275 | 2.75 | 0.146 | 1821 | 36 |  |  | 62ST2115 | 1.15 | 0.215 | 834 | 76
32SA2200 | 2 | 0.169 | 1359 | 49 |  |  | 62SB3700 | 0.7 | 0.245 | 644 | 100
32SA2170 | 1.7 | 0.167 | 1395 | 48 |  |  | 62ST3505 | 0.505 | 0.215 | 837 | 77
32SB2114 | 1.14 | 0.174 | 1279 | 51 |  |  | 62SQ3286 | 0.286 | 0.222 | 783 | 81
32SB3700 | 0.7 | 0.16 | 1523 | 45 |  |  | 62SQ3200 | 0.2 | 0.227 | 750 | 86
32SQ3472 | 0.472 | 0.177 | 1232 | 52 |  |  | 62SQ3150 | 0.15 | 0.227 | 751 | 86
32SQ3374 | 0.374 | 0.183 | 1153 | 55 |  |  | 62SQ3100 | 0.1 | 0.257 | 586 | 111
32SQ3293 | 0.293 | 0.179 | 1206 | 53 |  |  | 62SP4775 | 0.0775 | 0.25 | 618 | 104
32SQ3200 | 0.2 | 0.146 | 1825 | 37 |  |  | 62SP4561 | 0.0561 | 0.263 | 560 | 116
32SQ3150 | 0.15 | 0.153 | 1666 | 41 |  |  | 62SP4402 | 0.0402 | 0.277 | 505 | 130
32SQ3100 | 0.1 | 0.173 | 1307 | 53 |  |  | 62SP4281 | 0.0281 | 0.292 | 456 | 147
32SP4734 | 0.0734 | 0.174 | 1284 | 52 |  |  | 62SC4200 | 0.02 | 0.285 | 476 | 135
32SP4583 | 0.0583 | 0.172 | 1319 | 52 |  |  | 62SC4130 | 0.013 | 0.304 | 419 | 156
32SP4458 | 0.0458 | 0.178 | 1235 | 56 |  |  | 62SC5818 | 0.00818 | 0.331 | 354 | 187
32SC4324 | 0.0324 | 0.184 | 1145 | 57 |  |  | 62SC5516 | 0.00516 | 0.364 | 294 | 230
[7 empty] | 62SC5324 | 0.00324 | 0.402 | 242 | 290
[7 empty] | 62SC5204 | 0.00204 | 0.496 | 159 | 438
|  |  |  | 44.2857 |  |  | 62SC5128 | 0.00128 | 0.543 | 469 | 516
49.6429

## SR Cable Typical Allowances (hidden)
Recommended Valve Allowance |  | Recommended Flange Allowance
Pipe Diameter | Heating Cable Feet | Pipe Diameter | Heating Cable Feet
0.25 | 0.3 | 0.25 | 0.041667
0.5 | 0.8 | 0.5 | 0.083333
0.75 | 1.3 | 0.75 | 0.125
1 | 2 | 1 | 0.16667
1.25 | 3.3 | 1.25 | 0.20833
1.5 | 4.3 | 1.5 | 0.25
2 | 4.3 | 2 | 0.33333
2.5 | 4.3 | 2.5 | 0.41667
3 | 4.3 | 3 | 0.5
3.5 | 4.3 | 3.5 | 0.58333
4 | 4.3 | 4 | 0.66667
6 | 5 | 6 | 1
8 | 5 | 8 | 1.3333
10 | 5.6 | 10 | 1.6667
12 | 6.45 | 12 | 2
14 | 7.3 | 14 | 2.3333
16 | 8.35 | 16 | 2.6667
18 | 9.4 | 18 | 3
20 | 10.47 | 20 | 3.3333
24 | 12.6 | 24 | 4

## Typical Allowances (hidden)
Pipe Diameter | Heating Cable Feet | Pipe Diameter | Heating Cable Feet | Pipe Diameter | Light valve (flanged) | Light valve (threaded or welded) | Heavy valve (flanged) | Heavy valve (threaded or welded) | Typical Pipe Shoe | Flange (pair) | Field variance
0.25 | 0.3 | 0.25 | 0.041667 | 0.5 | 1 | 1 | 1 | 1 | 3 | 1 | 1.02
0.5 | 0.8 | 0.5 | 0.083333 | 0.75 | 1.5 | 1 | 1.5 | 1 | 3 | 1 | 1.02
0.75 | 1.3 | 0.75 | 0.125 | 1 | 2 | 1 | 2 | 1 | 3 | 1.5 | 1.02
1 | 2 | 1 | 0.16667 | 1.5 | 2.5 | 1.5 | 3 | 1.5 | 3 | 1.5 | 1.02
1.25 | 3.3 | 1.25 | 0.20833 | 2 | 2.5 | 2 | 3.5 | 2 | 3 | 1.5 | 1.02
1.5 | 4.3 | 1.5 | 0.25 | 3 | 3 | 2.5 | 4 | 2.5 | 3 | 2 | 1.03
2 | 4.3 | 2 | 0.33333 | 4 | 4 | 3 | 5 | 3 | 3 | 2 | 1.03
2.5 | 4.3 | 2.5 | 0.41667 | 6 | 5 | 3.5 | 6 | 3.5 | 3 | 2 | 1.03
3 | 4.3 | 3 | 0.5 | 8 | 7 | 4 | 8 | 4 | 3 | 2 | 1.03
3.5 | 4.3 | 3.5 | 0.58333 | 10 | 8 | 5 | 10 | 5 | 3 | 3 | 1.03
4 | 4.3 | 4 | 0.66667 | 12 | 9 | 6 | 12 | 6 | 3 | 3.5 | 1.03
6 | 5 | 6 | 1 | 14 | 10 | 7 | 14 | 7 | 4.5 | 4 | 1.03
8 | 5 | 8 | 1.3333 | 16 | 11 | 8 | 16 | 8 | 4.5 | 4.5 | 1.03
10 | 5.6 | 10 | 1.6667 | 18 | 12 | 9 | 18 | 9 | 4.5 | 5.5 | 1.03
12 | 6.45 | 12 | 2 | 20 | 13 | 10 | 20 | 10 | 4.5 | 6 | 1.03
14 | 7.3 | 14 | 2.3333 | 24 | 15 | 12 | 24 | 12 | 4.5 | 7 | 1.03
16 | 8.35 | 16 | 2.6667
18 | 9.4 | 18 | 3
20 | 10.47 | 20 | 3.3333
24 | 12.6 | 24 | 4

## Connection Kits & Accessories (hidden)
Component | Catalog Number | Quantity Breakdown | Pipe Straps
Power Connection (single heating cable) | JBS-100-A | 1 per circuit | 1
End Seal (above insulation) | E-100 | 1 per power connection plus one per tee | 1
Controller | 910*E1WL*SSR2 | 1 per circuit (system specific) | 0
RTD1 | RTD10CS | 1 per circuit (system specific) | 0
RTD2 | RTD4AL | 1 per circuit (system specific) | 1
GT-66 Attachment Tape Requirements |  | ETL (Electric Traced Label)
Pipe Diameter | Rolls/100ft of Cable | Quantity Breakdown | ETL/foot
0.25 | 0.3 | One label every 10 feet | 0.1
0.5 | 0.6
0.75 | 0.9
1 | 1.2
1.25 | 1.9
1.5 | 2.6
2 | 4
2.5 | 4
3 | 4
3.5 | 5
4 | 6
6 | 8
8 | 10
10 | 10
12 | 10
14 | 10
16 | 10
18 | 10
20 | 10
24 | 10
SR Cable Pipe Strap Selection |  | MI Cable Pipe Strap Selection
Pipe Size | Catalog Number | Pipe Size | Catalog Number | Package QTY
0.5 | PS-03 | 0.5 | PB 125 | 50
0.75 | PS-03 | 0.75 | PB 125 | 50
1 | PS-03 | 1 | PB 300 | 35
1.5 | PS-03 | 1.5 | PB 300 | 35
2 | PS-10 | 2 | PB 300 | 35
2.5 | PS-10 | 2.5 | PB 300 | 35
3 | PS-10 | 3 | PB 300 | 35
3.5 | PS-10 | 3.5 | PB 600 | 25
4 | PS-10 | 4 | PB 600 | 25
6 | PS-10 | 6 | PB 600 | 25
8 | PS-10 | 8 | PB 1000 | 1
10 | PS-10 | 10 | PB 1000 | 1
12 | PS-20 | 12 | PB 1200 | 1
14 | PS-20 | 14 | PB 2400 | 1
16 | PS-20 | 16 | PB 2400 | 1
18 | PS-20 | 18 | PB 2400 | 1
20 | PS-20 | 20 | PB 2400 | 1
24 | PS-20 | 24 | PB 2400 | 1

## Component Descriptions (hidden)
Cable Description | Design Temperature | Catalog Number
10 W/ft, 120V Self-Reg Heating Cable | 250 | 10XTV1-CT-T3
5 W/ft, 120V Self-Reg Heating Cable | 250 | 5XTVR1-CT-T2
15 W/ft, 120V Self-Reg Heating Cable | 250 | 15XTVR1-CT-T3
10 W/ft, 120V Self-Reg Heating Cable | 140 | 10BTV1-CT
10 W/ft, 120V Self-Reg Heating Cable | 225 | 10QTVR1-CT
15 W/ft, 120V Self-Reg Heating Cable | 225 | 15QTVR1-CT
3 W/ft, 120V Self-Reg Heating Cable | 140 | 3BTV1-CT
5 W/ft, 120V Self-Reg Heating Cable | 140 | 5BTV1-CT
8 W/ft, 120V Self-Reg Heating Cable | 140 | 8BTV1-CT
10 W/ft, 120V Self-Reg Heating Cable | 360 | 10VPL1-CT
15 W/ft, 120V Self-Reg Heating Cable | 360 | 15VPL1-CT
5 W/ft, 120V Self-Reg Heating Cable | 360 | 5VPL1-CT
20 W/ft, 120V Self-Reg Heating Cable | 360 | 20VPL1-CT
300V Pyrotenax Dual Conductor MI Heating Cable | 690+ | 32 Series MI
600V Pyrotenax Dual Conductor MI Heating Cable | 800+ | 62 Series MI
Accessory Description | Catalog Number
Above-Insulation End Seal Kit | E-100-A
Single Entry Power Kit with J. Box | JBS-100-A
DigiTrace 910 1pt Controller, 2 pole 30A 277V SSR | 910*E1WL*SSR2
DigiTrace RTD with 10 foot S/S Corrugated Shield | RTD10CS
Electrical Traced Label for traced pipes and tanks | ETL-ENGLISH
Glass Tape (66ft/roll) (Not for Stainless-Steel Pipe) | GT-66
Pipe strap 1-3 in. | PS-3
Pipe strap 3-10 in. | PS-10
Pipe strap 10-20 in. | PS-20
Pipe Straps for MI Cables - 1 to 3 in. (package of 35 pc) | PB300
Pipe Straps for MI Cables - 3 to 6 in. (package of 25 pc) | PB600
Pipe Straps for MI Cables - 8 to 10 in. | PB1000
Pipe Straps for MI Cables - 10 to 12 in. | PB1200
Ferralloy Junction Box, CID1, 3 Hubs | PTJB
DigiTrace RTD, -100F to 900F, Pipe Mount | RTD4AL

## QCS
QUOTE COMPARISON SHEET - SUBCONTRACT
Primary DOR: Technical Staff pink sections, Procurement Staff everything else. | [5 empty] | Owner AVL Status:
- Heat Trace Sub | [5 empty] | BID DUE: | [6 empty] | 2014-06-20 |  |  |  | 2014-06-20 |  |  |  |  | 2014-06-20
[6 empty] | RFP SENT: | KIEWIT DESIGN AND INSTALL | [5 empty] | 2014-06-05 |  |  |  | 2014-06-05 |  |  |  |  | 2014-06-05
[6 empty] | BID DURATION: | [9 empty] | Days |  | 15 |  |  | Days |  | 15 |  |  | Days
| Project No.: | [5 empty] | Self Performed | [5 empty] | BIDDER 1 |  |  |  | BIDDER 2 |  |  |  |  | BIDDER 3
| Project Name: |  |  |  |  | Bidder Legal Name:
| Owner: |  |  |  |  | Bidder Contact Name:
| Job Site: |  |  |  |  | Bidder Contact Email:
| RFP Description: | Heat Trace Sub |  |  |  | Bidder Phone:
| Spec: |  |  |  |  | Bid Date or "No Bid":
| HD Quote Group Tag: |  |  |  |  | Bid Valid Until Date:
| Engineering: |  |  |  |  | Bid Validity Duration (Days): | 0
| Procurement: |  |  |  |  | Firm or Budgetary Bid:
| Reviewer: |  |  |  |  | Bidder Proposal Reference No.:
| QCS Revision #/ Date: | A |  |  |  | Quoted Currency: | USD - US Dollar | [5 empty] | USD - US Dollar |  |  |  | USD - US Dollar |  |  |  |  | USD - US Dollar
| Project Currency: | USD - US Dollar |  |  |  | Exchange Rate (1 : $xUSD - US Dollar) | 1 | [5 empty] | 1 |  |  |  | 1 |  |  |  |  | 1
TOTAL PROPOSAL PRICE |  |  |  |  | - | - | - | - | - | - | - | 1707259.8233 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
Pricing Breakdown |  |  |  |  | Qty. | Unit | Unit Price (USD - US Dollar) | $/MH | UR/UOM | Labor Total | Material Total | Total Price (USD - US Dollar) | Unit Price (USD - US Dollar) | Labor Total | Material Total | Total Price (USD - US Dollar) | Unit Price (USD - US Dollar) | Definition | Labor Total | Material Total | Total Price (USD - US Dollar) | Unit Price (USD - US Dollar) | Definition | Labor Total | Material Total | Total Price (USD - US Dollar) | Pricing Breakdown | Cost
Labor / Material Quoted |  |  |  |  | - | - | - | - | - | - | - | 1633179.9883 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | Heat Trace Design/Engineering |  |  |  | 361 | EA |  | 175 |  | 63175 |  | 63175 | [14 empty] | Heat Trace Design/Engineering | 63175
2 | OEM Manuals |  |  |  | 1 | LOT |  |  |  |  | 15000 | 15000 | [14 empty] | OEM Manuals | 15000
3 | Heat Trace Materials | [25 empty] | Equipment / Facilities / Safety | 14248.633
4 | Control Panels |  |  |  | 9 | EA | 18200 | 37 | 3.6 | 1198.8 | 163800 | 164998.8 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Heat Trace Material Cost | 814076.0723
5 | Transformers |  |  |  | 9 | EA | 4200 | 37 | 5.49 | 1828.17 | 37800 | 39628.17 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Heat Trace Installation Labor | 527199.421
6 | Heat Trace (Self Regulating Cable, MI Cable. Accessories Included) |  |  |  | 24599 | LF |  | 37 | 0.329 | 299443.627 | 528533.2123 | 827976.8393 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Standard Commercial Items | 74079.835
7 | Electrical Materials | [25 empty] | Indirect Cost | 199480.862
8 | Conduit |  |  |  | 7220 | LF | 5.96 | 37 | 0.5 | 133570 | 43103.4 | 176673.4 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | G & A | 0
9 | Wire and Cable |  |  |  | 39400 | LF | 1.48 | 37 | 0.038 | 55396.4 | 36124 | 91520.4 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | Margin | 0
10 | Terminations |  |  |  | 2346 | EA | 1.94 | 37 | 0.412 | 35762.424 | 4715.46 | 40477.884 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
11 | ST&S |  |  |  | 14248.633 | MH |  | 1 |  |  | 14248.633 | 14248.633 | [14 empty] | Total Cost | 1707259.8233
12 | Indirect Cost
13 | Craft | 3
14 | Staff | 1
15 | Craft to Staff Ratio |  | 3 |  | 4749.5443 | MH |  | 42 |  | 199480.862 |  | 199480.862
16 | Indirect Cost
17
18 | G & A | 0% |  |  | 1 | LOT |  |  |  | 0 |  | 0
19 | Margin | 0% |  |  | 1 | LOT |  |  |  | 0 |  | 0
20
20
21
22
23
24
25
26
27
28 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
29 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
30 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
31 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
32 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
33 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
34 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
35 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
36 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
37 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
38 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
39 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
40 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
41 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
42 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
43 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
44 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
45 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
46 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
47 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
48 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
49 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
50 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
51 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
52 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
53 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
54 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
55 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
56 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
57 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
58 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
59 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
60 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
61 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
62 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
63 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
64 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
65 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
66 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
67 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
68 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
69 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
70 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
71 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
72 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
73 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
74 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
75 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
76 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
77 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
78 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
79 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
80 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
81 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
82 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
83 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
84 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
85 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
86 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
87 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
88 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
89 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
90 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
91 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
92 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
93 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
94 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
95 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
96 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
97 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
98 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
99 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
100 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Options Requested or Offered |  |  |  |  | - | - | - | - | - | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | Warranty - for 1 Year beyond Owner's Requirement |  |  |  | 0 | LOT | [5 empty] | 0
2 | [11 empty] | 0
3 | [5 empty] | LOT | [5 empty] | 0
4 | [5 empty] | LOT | [5 empty] | 0
5 | [5 empty] | LOT | [5 empty] | 0
6 | [5 empty] | LOT | [5 empty] | 0
7 | [5 empty] | LOT | [5 empty] | 0
8 | [5 empty] | LOT | [5 empty] | 0
9 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
10 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Standard Commercial Items |  |  |  |  | - | - | - | - | - | - | - | 74079.835 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | Sales/ Use Tax |  |  | Not Required |  | LOT | [5 empty] | 0
2 | Freight (DDP Jobsite - Incoterms 2010) |  |  | Required | 1 | LOT | 41416.2353 |  |  |  |  | 41416.2353
3 | Warranty - Standard (See 2.0 Below) |  |  | Required | 1 | LOT | 32663.5998 |  |  |  |  | 32663.5998
4 | Warranty - Adder to meet Owner's Terms (See 2.0 Below) |  |  | Required | 1 | LOT | [5 empty] | 0
5 | TFA - Startup & Erection Assistance Duration (Bidder to specify quantity) |  |  | Required |  | DAY | [5 empty] | 0
6 | TFA - Startup & Erection Assistance Round Trip (Bidder to specify quantity) |  |  | Required |  | RT | [5 empty] | 0
7 | TFA - Training Duration (Bidder to specify quantity) |  |  | Required |  | DAY | [5 empty] | 0
8 | TFA - Training Round Trip (Bidder to specify quantity) |  |  | Required |  | RT | [5 empty] | 0
9 | Spares - Startup & Commissioning - (Bidder to provide detailed list) |  |  | Required | 1 | LOT | [5 empty] | 0
10 | Spares - Construction - (Bidder to provide detailed list) |  |  | Required | 1 | LOT | [5 empty] | 0
11 | Spares - Special Tools - (Bidder to provide detailed list) |  |  | Required | 1 | LOT | [5 empty] | 0
12 | Spares - 2-Year Operating - (Bidder to provide detailed list) |  |  | Not Required |  | LOT | [5 empty] | 0
13 | Security Cost (Bond for full contract price, Letter of Credit, Etc.) |  |  | Required | 0 | LOT | [5 empty] | 0
Commercial Adjustments |  |  |  |  | - | - | - | - | - | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
2 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
3 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
4 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
5 | [11 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Technical Adjustments |  |  |  |  | - | - | - | - | - | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
[6 empty] | LOT | [5 empty] | 0
[6 empty] | LOT | [5 empty] | 0
[6 empty] | LOT | [5 empty] | 0
[6 empty] | LOT | [5 empty] | 0
[6 empty] | LOT | [5 empty] | 0
TOTAL PROPOSAL PRICE |  |  |  |  | - | - | 74079.835 | - | - | 789855.283 | 828324.7053 | 1707259.8233 | #REF! | 0 | #REF! | 0 | - | - | 0 | #REF! | 0 | - | - | 0 | #REF! | 0
TOTAL PROPOSAL PRICE (Not Including Security) |  |  |  |  | - | - | - | - | - | - | - | 1707259.8233 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
TOTAL UNIT PRICE (Not Including Security) - Enter In Hard Dollar | [5 empty] | - | - | - | - | - | - |  | - | - | - |  | - | - | - | - |  | - | - | - | -
Security Cost Per $1000 - Enter In Hard Dollar |  |  |  |  | - | Per $1000 | - | - | - | - | - | 0 | - | - | - |  | - | - | - | - |  | - | - | - | -
Evaluation Factors (constructability, past performance, etc.) |  |  |  |  | - | - | - | - | - | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
2 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
3 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
4 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
5 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
TOTAL EVALUATED PRICE |  |  |  |  | - | - | - | - | - | - | - | 1707259.8233 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
Options Excluded |  |  |  |  | - | - | - | - | - | - | - | 0 | - | - | - | 0 | - | - | - | - | 0 | - | - | - | - | 0
1 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
2 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
3 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
4 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
5 | [5 empty] | LOT | [5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
Commercial Items Requirements
1.0 Financial Security
| Specify type of security instrument provided (select from drop-down list) | [11 empty] | 100% Supply Bond |  |  |  | 100% Supply Bond |  |  |  |  | 100% Supply Bond
| Rate per $1,000 of coverage: | [11 empty] | Not Provided - Plugged 1.5% for 100% Bond |  |  |  | Not Provided - Plugged 1.5% for 100% Bond |  |  |  |  | Not Provided - Plugged 1.5% for 100% Bond
| Bidder's Surety Firm: | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Bonding Capacity: | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
2.0 Warranty
| Specify Bidder's Standard Warranty terms included in Bidder's Base Price | [11 empty] | 12 mo. From delivery / plug 2% for add'l yr |  |  |  | 12 mo. From delivery / plug 2% for add'l yr |  |  |  |  | 12 mo. From delivery / plug 2% for add'l yr
| Confirm Standard Warranty with price Adder above will meet Owner's terms of 12 months from Substantial | [11 empty] | Confirmed |  |  |  | Confirmed |  |  |  |  | Confirmed
| Completion of: | Summer 2017
3.0 Site Specific Requirements
| Is Safety training and orientation included in your proposal? (select from drop-down list) | [11 empty] | No |  |  |  | No |  |  |  |  | No
| Are background checks included in your proposal? | [11 empty] | No - see attached comments |  |  |  | No - see attached comments |  |  |  |  | No - see attached comments
| Are employee drug testing costs included in your proposal? | [11 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
[13 empty] | Supply Only |  |  |  | Supply Only |  |  |  |  | Supply Only
4.0 Shipping and Schedule of Work
| Lead Time - Drawings ARO (Include 2 Weeks for Drawing Approval) | [11 empty] | 6-8 weeks |  |  |  | 6-8 weeks |  |  |  |  | 6-8 weeks
| Lead Time - Equipment/Material to Jobsite ARAD | [11 empty] | 10-12 weeks |  |  |  | 10-12 weeks |  |  |  |  | 10-12 weeks
| Lead Time - Installation / Erection (mobilization to demobilization) | [11 empty] | 16-20 weeks |  |  |  | 16-20 weeks |  |  |  |  | 16-20 weeks
| Schedule - Number of Craft Workers required | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Hours worked per day | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Number of days worked per week | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Schedule - Total estimated man-hours | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
| Labor - Union or Non-Union | [11 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
5.0 Bidder Certification - Technical, Business, Diversity, Etc.
Bidder's Primary Certification (select from drop-down list)
Additional Certification (select from drop-down list)
6.0 Proposal Requirements - Insurance, Safety, Quality, and Licensing
| Can Bidder meet Insurance requirements as specified in RFP? (select from drop-down list) | [11 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| Does Bidder have written Quality Assurance program? (select from drop-down list) | [11 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| Does Bidder have written Safety Program? (select from drop-down list) | [11 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
| EMR and Frequency/Severity Rates for last 3 years | [5 empty] | Year 1 | Year 1 | Year 1 | Year 1 | Year 1 | Year 3 | Year 1 | Year 1 | Year 1 | Year 3 | Year 1 | Year 2 | Year 1 | Year 1 | Year 3 | Year 1 | Year 2 | Year 1 | Year 1 | Year 3
EMR Rates:
Frequency / Severity Rates:
Is your Company currently licensed in the State where Project is located?
[13 empty] | Not Provided in Proposal |  |  |  | Not Provided in Proposal |  |  |  |  | Not Provided in Proposal
7.0 Proposal Exception
| Does Bidder Proposal comply with Instructions to Bidders? (select from drop-down list) | [11 empty] | Yes |  |  |  | Yes |  |  |  |  | Yes
8.0 Proposed Progress Payment Milestones |  |  |  | Percentage of Contract Total |  |  | Description of Milestone |  |  | Description of Milestone |  | % of Contract Price | Description of Milestone |  |  | % of Contract Price | Description of Milestone |  |  |  | % of Contract Price | Description of Milestone |  |  |  | % of Contract Price
1st Milestone
| 2nd Milestone | 2nd Milestone
| 3rd Milestone | 3rd Milestone
| 4th Milestone | 4th Milestone
| 5th Milestone | 5th Milestone
| 6th Milestone | 6th Milestone
| 7th Milestone | 7th Milestone
| 8th Milestone | 8th Milestone
| 9th Milestone | 9th Milestone
| 10th Milestone | 15th Milestone
Technical Design Conditions |  |  |  | Per RFP/ EPC Contract |  |  | - | [5 empty] | - |  |  |  | - |  |  |  |  | -
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
Additional Technical and Commercial Information/Clarifications/Exceptions | [6 empty] | - | [5 empty] | - |  |  |  | - |  |  |  |  | -
1
2
3
4
5
Comparison of Total Proposal Prices | [6 empty] | - | [5 empty] | - |  |  |  | - |  |  |  |  | -
1 | [5 empty] | Amount above minimum bid:
2 | [5 empty] | Percent above minimum bid:
Pricing Reliability Indicator (Low Plug = High Reliability) | [6 empty] | - | [5 empty] | - |  |  |  | - |  |  |  |  | -
1 | Dollar and % of Amount Plugged | [5 empty] | Plug $ | Plug $ | Plug $ | Plug $ | Plug $ | Total Price | Plug $ | Plug $ | Plug $ | Total Price | Plug $ | Plug % | Plug $ | Plug $ | Total Price | Plug $ | Plug % | Plug $ | Plug $ | Total Price
[7 empty] | #REF! | 0 | #REF! | #REF! | #REF! | 1707259.8233 | #REF! | #REF! | #REF! | 0 | 0 |  | #REF! | #REF! | 0 | 0 |  | #REF! | #REF! | 0
Awarding | [6 empty] | - | [5 empty] | - |  |  |  | - |  |  |  |  | -
1 | Technically Acceptable ("Yes"/"No") | [11 empty] | YES |  |  |  | YES |  |  |  |  | YES
2 | If No, Explain…
3 | Commercially Acceptable ("Yes"/"No") | [11 empty] | YES |  |  |  | YES |  |  |  |  | YES
4 | If No, Explain…
5 | Price Carried In Estimate ("Yes"/"No")
6 | If technically and commercially acceptable but low price is not carried, Explain…
7 | Alternate Price ("Yes"/"No")
8 | If technically and commercially acceptable but next low price is not an alternate, Explain…
9 | Enter any additional notes that might help others (now and many years into the future) understand fully the team's evaluation, observation and reasoning (without having to track someone down or relying on one's memories)
Note on D33: Administrator: Get the JRO from the indirect lead. Typically the JRO is 3:1
Note on F33: Administrator:
Note on D38: Administrator: Get the G&A and margin from the indirect lead.
Note on B184: Warranty duration and Substantial Completion date came from data specified on ITB

## Vendor Pipe Benchmark
OEM Type | Vendor | Class | Job | Code | Status | Configuration | Location | Pipe LF | Circuit QTY (EA) | SR Cable LF | MI Cable LF | Heater LF/Pipe LF | Job | Configuration
CTG | GE | 7FA.05 | Woodbridge | CTG-Woodbridge | Production | 2x1 | Outdoor |  | 35 | 500 |  |  | Allen | 2x1
CTG | GE | 7HA.02 | Allen | CTG-Allen |  | 2x1 | Outdoor | [5 empty] | Cherokee | 2x1
CTG |  |  | Cherokee | CTG-Cherokee |  | 2x1 | Outdoor | [5 empty] | Lackawanna | 3x1
CTG |  | 7FA.05 | Paradise | CTG-Paradise |  | 3x1 | Outdoor | [5 empty] | Mattawoman | 3x1
CTG |  | 7HA.02 | Lackawanna | CTG -Lackawanna |  | 3x1 | Outdoor | [5 empty] | Paradise | 3x1
CTG | Siemens |  | Mattawoman | CTG-Mattawoman | Estimate | 3x1 | Outdoor | [5 empty] | Woodbridge | 2x1
HRSG | CMI |  | Woodbridge | HRSG-Woodbridge | Production | 2x1 | Outdoor |  | 40 |  | 5354 |  | Cove Point | 2x2
HRSG | Vogt |  | Allen | HRSG-Allen |  | 2x1 | Outdoor | [5 empty] | North Battleford | 1x1
HRSG |  |  | Cherokee | HRSG-Cherokee |  | 2x1 | Outdoor
HRSG | Vogt |  | Paradise | HRSG-Paradise |  | 3x1 | Outdoor
HRSG |  |  | Lackawanna | HRSG-Lackawanna |  | 3x1 | Outdoor
HRSG | NEM |  | Mattawoman | HRSG-Mattawoman | Estimate | 3x1 | Outdoor
Aux Boiler | Nebraska |  | Woodbridge | Aux Boiler-Woodbridge | Production | 2x1 | Outdoor |  | 16 |  | 2000
Aux Boiler |  |  | Allen | Aux Boiler-Allen |  | 2x1 | Outdoor
Aux Boiler |  |  | Cherokee | Aux Boiler-Cherokee |  | 2x1 | Outdoor
Aux Boiler |  |  | Paradise | Aux Boiler-Paradise |  | 3x1 | Outdoor
Aux Boiler |  |  | Lackawanna | Aux Boiler-Lackawanna |  | 3x1 | Outdoor
Aux Boiler |  |  | Mattawoman | Aux Boiler-Mattawoman | Estimate | 3x1 | Outdoor
STG |  |  | Woodbridge | STG-Woodbridge | Production | 2x1 | Indoor |  |  | 0
STG | Toshiba |  | Allen | STG-Allen |  | 2x1 | Indoor |  |  | 0
STG |  |  | Cherokee | STG-Cherokee |  | 2x1 | Indoor |  |  | 0
STG | Toshiba |  | Paradise | STG-Paradise |  | 3x1 | Indoor |  |  | 0
STG |  |  | Lackawanna | STG-Lackawanna |  | 3x1 | Indoor |  |  | 0
STG | Siemes |  | Mattawoman | STG-Mattawoman | Estimate | 3x1 | Indoor |  |  | 0
Condenser |  |  | Woodbridge | Condenser-Woodbridge | Production | 2x1 | Outdoor |  | 30 | 3000
Condenser |  |  | Allen | Condenser-Allen |  | 2x1 | Outdoor
Condenser |  |  | Cherokee | Condenser-Cherokee |  | 2x1 | Outdoor
Condenser |  |  | Paradise | Condenser-Paradise |  | 3x1 | Outdoor
Condenser |  |  | Lackawanna | Condenser-Lackawanna |  | 3x1 | Outdoor
Condenser |  |  | Mattawoman | Condenser-Mattawoman | Estimate | 3x1 | Outdoor
ACC | SPX |  | Cove Point | ACC-Cove Point |  | 2x2 | Outdoor |  | 3 | 500
ACC |  |  | North Battleford | ACC-North Battleford |  | 1x1 | Outdoor
BFP |  |  | Woodbridge | BFP-Woodbridge | Production | 2x1 | Outdoor |  | 30 |  | 136
-
-
Note on I1: Pipe and Heater lengths are for each piece of equipment. i.e 1 ea CTG, HRSG, STG, Condenser and Aux Boiler

## System Graphs
System Code | Pipe Length (LF) | Heater Cable Length (LF)
AXS | 456 | 888 | 1.9
BFW | 1840 | 3304 | 1.8
CND | 786 | 1116 | 1.4
CTP | 54 | 125 | 2.3
DWS | 672 | 1307 | 1.9
DWT | 4 | 25 | 6.3
HPS | 62 | 320 | 5.2
HRH | 590 | 942 | 1.6
PDR | 8 | 23 | 2.9
PWS | 67 | 298 | 4.4
SDR | 93 | 142 | 1.5
WDR | 44 | 118 | 2.7